Technical Glass Products has included notes in this specification to assist you in tailoring the content to your project.  These comments will appear on your screen in blue.  To hide them and view only the specification, do the following:

Click the “Office” button and then click the word “Options” OR select the “File” and then click “Options”.   Click “Display” at the left of the dialog box.  Remove the check mark from the “Hidden Text” box.  Then click “OK.”  All blue text will then be hidden.

This document is designed for use by a qualified construction specifier. Proper modifications are required to tailor this specification to your project needs.  Optional text is placed between brackets “[ ].”  Blank underlines  “__” represent areas you need to fill in with your project specific information. For assistance, call Technical Glass Products at 1-800-426-0279.

This guide specification is a supplier-specific proprietary product specification using the proprietary method of specifying applicable to project specifications and master guide specifications. This Section specifies the “Fireframes Designer Series” a fire-rated steel frame system supplied by Technical Glass Products further described in Part 2 – Products.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

SECTION 08 41 23 - FIRE RATED GLASS AND FRAMING SYSTEMS – FIREFRAMES® DESIGNER SERIES

- GENERAL

      - SUMMARY

        - Section Includes:

          - Fire rated door and framing systems for installation as (choose one or more as applicable) [vision lights in fire rated doors] [full vision fire rated doors] [sidelights] [borrowed lights] [windows] [transoms] in [exterior] [and] [interior] openings.

        - Related Sections include the following:

Verify that Section titles referenced below are correct for this Project's Specifications; Revise the Section number and title below to suit project requirements, specification practices and section content. Refer to CSI MasterFormat for other section numbers and titles.

Verify other nearby items are specified. These include concrete and masonry inserts, concealed flashing.

        - Related Sections:

          - Section 05 12 00 “Structural Steel Framing:” Steel attachment members

          - Section 05 50 00  “Metal Fabrications:” Steel attachment members inserts and anchors

          - Section 07 25 00 “Weather Barriers:” Perimeter air, water and vapor seal between the work of this section and adjacent construction

          - Section 07 62 00 “Sheet Metal Flashing and Trim” Flashing between this work and other work

          - Section 07 84 00 “Firestopping:” Firestops between work of this section and other fire resistive assemblies.

          - Section 08 11 13 “Hollow Metal Doors and Frames.” Hollow Metal doors prepped for the work of this section.

          - Section 08 71 00 “Door Hardware:” Door hardware other than that provided by the work of this section

          - Section 08 71 13 “Automatic Door Operators” opener for door to comply with ADA and Local Authority opening force requirements.

      - REFERENCES

Adjust lists below to suit Project.. Specifically this means to delete the types of finish that are not used AAMA 2603 thru 2605 and if the system is used in interior applications all the air and water infiltration testing and standards may be removed.

        - American Architectural Manufacturers Association (AAMA)

          - AAMA 501.1-2005: Standard Test Method for Water Penetration of Windows, Curtain Walls, and Doors Using Dynamic Pressure

          - AAMA 501.2-2003: Quality Assurance and Diagnostic Water Leakage Field Check of Installed Storefronts, Curtain Walls, and Sloped Glazing Systems

          - AAMA 501.5-2005: Test Method for Thermal Cycling of Exterior Walls

          - AAMA 1503-1998: Voluntary Test Method for Thermal Transmittance and Condensation Resistance of Windows, Doors and Glazed Wall Sections

          - AAMA 2603-2002 - Voluntary Specification, Performance Requirements and Test Procedures for Pigmented Organic Coatings on Aluminum Extrusions and Panels.

          - AAMA 2604-2005 - Voluntary Specification, Performance Requirements and Test Procedures for High Performance Organic Coatings on Aluminum Extrusions and Panels.

          - AAMA 2605-2005 - Voluntary Specification, Performance Requirements and Test Procedures for Superior Performing Organic Coatings on Aluminum Extrusions and Panels.

        - American Society for Testing and Materials (ASTM):

          - Material related

            - ASTM A 1008/A 1008M - Standard Specification for Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength, Low Alloy, and High-Strength Low-Alloy with Improved Formability, Solution Hardened, and Bake Hardenable; 2007.

            - ASTM A 1011/A 1011M - Standard Specification for Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy and High-Strength Low-Alloy with Improved Formability, and Ultra-High Strength; 2006b.

          - Exterior related

            - ASTM E 283-04: Test Method for Determining the Rate of Air Leakage through Exterior Windows, Curtain Walls, and Doors under Specified Pressure Differences across the Specimen

            - ASTM E 330-02: Test Method for Structural Performance of Exterior Windows, Doors, Skylights and Curtain Walls by Uniform Static Air Pressure Difference Procedure A

            - ASTM E 331-04: Test Method for Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform Static Air Pressure Difference

            - ASTM E 783-02: Test Method for Field Measurement of Air Leakage through Installed Exterior Windows and Doors

            - ASTM E 1105-00: Test Method for Field Determination of Water Penetration of Installed Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform or Cyclic Static Air Pressure Difference

          - Sound related:

            - ASTM E 90-04: Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements

            - ASTM E 413-04: Standard Classification for Rating Sound Insulation

        - American Welding Society (AWS)

          - AWS D1.3 - Structural Welding Code - Sheet Steel; 2007

        - Builders Hardware Manufacturers Association, Inc.

          - BHMA A156 - American National Standards for door hardware; 2006 (ANSI/BHMA A156).

        - Canadian Standards

          - CAN-S101 Fire Endurance Tests of Building Construction and Materials

          - CAN4-S104 Fire Tests of Door Assemblies

          - CAN4-S106 Standard Method for Fire Tests of Window and Glass Block Assemblies

        - National Fire Protection Association (NFPA):

          - NFPA 80:  Standard for Fire Doors and Fire Windows.

          - NFPA 251:  Standard Methods of Tests of Fire Endurance of Building Construction and Materials.

          - NFPA 252:  Standard Methods of Fire Tests of Door Assemblies.

          - NFPA 257:  Standard on Fire Test for Window and Glass Block Assemblies.

        - Underwriters Laboratories, Inc. (UL):

          - UL 9:  Fire Tests of Window Assemblies.

          - UL 10B:  Fire Tests of Door Assemblies.

          - UL 10C:  Positive Pressure Fire Tests of Door Assemblies.

        - American National Standards Institute (ANSI):

          - ANSI Z97.1:  Standard for Safety Glazing Materials Used in Buildings.

        - Consumer Product Safety Commission (CPSC):

          - CPSC 16 CFR 1201 Categories I and II:  Safety Standard for Architectural Glazing Materials.

        - American Society of Civil Engineers (ASCE)

          - ASCE 7 – Minimum Design Loads for Buildings and Other Structures; 2005

        - New York City approval

          - MEA# 242-00-M

      - DEFINITIONS

        - Manufacturer:  A firm that produces primary glass, fabricated glass or framing as defined in referenced glazing publications.

      - SUBMITTALS

        - Submit in accordance with Section <Insert Section #>.

        - Product Data:

          - Technical Information:  Submit latest edition of manufacturer’s product data providing product descriptions, technical data, Underwriters Laboratories, Inc. listings and installation instructions.

        - Shop Drawings:

          - Include plans, elevations and details of product showing component dimensions; framed opening requirements, dimensions, tolerances, and attachment to structure

        - Hardware schedule: list of manufacture supplied hardware and verification of cylinder size complying with Section 08 71 00

        - Samples (optional):   For following products:

          - Glass sample-as provided by manufacturer

          - Sample of frame

          - Verification of sample of selected finish

        - Glazing Schedule:  Use same designations indicated on drawings for glazed openings in preparing a schedule listing glass types and thicknesses for each size opening and location.

        - Warranties: Submit manufacturer’s warranty.

        - Certificates of compliance from glass and glazing materials manufacturers attesting that glass and glazing materials furnished for project comply with requirements.

          - Separate certification will not be required for glazing materials bearing manufacturer’s permanent label designating type and thickness of glass, provided labels represent a quality control program involving a recognized certification agency or independent testing laboratory acceptable to authority having jurisdiction.

      - QUALITY ASSURANCE

        - Testing Agency Qualifications: Qualified according to

          - International Accreditation Service for a Type A Third-Party Inspection Body (Field Services ICC-ES Third-Party Inspections Standard Operating Procedures, 00-BL-S0400 and S0401)

          - International Accreditation Service for Testing Body-Building Materials and Systems

            - Fire Testing

              - ASTM Standard  E 119

              - CPSC Standard 16 CFR 1201

              - NFPA Standards 251, 252, 257

              - UL Standards 9, 10B, 10C, 1784, UL Subject 63

              - BS 476; Part 22:  1987

              - EN 1634-1

              - CAN Standards S 101, S 104, S 106

        - Installer Qualifications:  An experienced installer who has completed glazing similar in material, design, and extent to that indicated for this Project; whose work has resulted in glass installations with a record of successful in-service performance; and who employs glass installers for this Project who are certified under the National Glass Association Glazier Certification Program as Level 2 (Senior Glaziers) or Level 3 (Master Glaziers).

Delete paragraph above or below.  If retaining above, verify with prospective installers that they can comply with glazier certification requirements.

        - Installer Qualifications:  An experienced installer who has completed glazing similar in material, design, and extent to that indicated for Project and whose work has resulted in construction with a record of successful in-service performance.

        - Source Limitations for Glazing Accessories:  Obtain framing system, glazing and glazing accessories from one source for each product and installation method indicated.

        - Fire-Rated Door Assemblies:  Assemblies complying with NFPA 80 that are classified and labeled by UL, for fire ratings indicated, based on testing according to NFPA 252.  Assemblies must be factory-welded or come complete with factory-installed mechanical joints and must not require job site fabrication.

Retain paragraph above for doors and paragraph below for windows if wire glass or another fire-resistive glazing product is specified in Part 2.

        - Fire-Rated Window Assemblies:  Assemblies complying with NFPA 80 that are classified and labeled by UL, for fire ratings indicated, based on testing according to NFPA 257.  Assemblies must be factory-welded or come complete with factory-installed mechanical joints and must not require job site fabrication.

Generally retain paragraph below unless types of glass selected do not require labeling by authorities having jurisdiction or if certification is required as well as labels.

        - Listings and Labels - Fire Rated Assemblies:  Under current follow-up service by Underwriters Laboratories® maintaining a current listing or certification. Label assemblies accordance with limits of manufacturer’s listing.

        - Regulatory Requirements:  Comply with provisions of the following:

Generally retain Americans with Disabilities Act Accessibility Guidelines below for private projects; FED-STD-795 for Federal, State, and local government projects.  Verify with authorities having jurisdiction.

          - Where indicated to comply with accessibility requirements, comply with [Americans with Disabilities Act (ADA), "Accessibility Guidelines for Buildings and Facilities (ADAAG),"] [ANSI A117.1,] [FED-STD-795, "Uniform Federal Accessibility Standards,"] as follows:

            - Handles, Pulls, Latches, Locks, and other Operating Devices:  Shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist.

            - Door Closers:  Comply with the following maximum opening-force requirements indicated:

              - Accessible doors no more than 5 lbf (22.2 N) push or pull force

              - Fire Doors:  Minimum opening force allowable by authorities having jurisdiction

          - Compliance with this standard requires auto openers to be added to the opening due to the weight of the doors. Coordinate the addition of auto-openers with the Division 8 section “Door Hardware” or other section containing these devices. Verify that the Authority Having Jurisdiction is using NFPA 101 and/or IBC and which edition dates of both as a requirement for the facility. NFPA 101:  Comply with the following for means of egress doors:

            - Latches, Locks, and Exit Devices:  Not more than 15 lbf (67 N) to release the latch.  Locks shall not require the use of a key, tool, or special knowledge for operation.

            - Door Closers:  Not more than 30 lbf (133 N) to set door in motion and not more than 15 lbf (67 N) to open door to minimum required width.

          - IBC 2012 Chapter 10 Means of Egress:  Comply with the following for means of egress doors:

            - Latches, Locks, and Exit Devices:  Not more than 15 lbf (67 N) to release the latch.  Locks shall not require the use of a key, tool, or special knowledge for operation.

            - Door Closers:  Not more than 30 lbf (133 N) to set door in motion and not more than 15 lbf (67 N) to open door to minimum required width.

      - DELIVERY, STORAGE AND HANDLING

        - Deliver, store and handle under provisions specified by manufacturer.

      - PROJECT CONDITIONS

        - Obtain field measurements prior to fabrication of frame units. If field measurements will not be available in a timely manner coordinate planned measurements with the work of other sections.

          - Note whether field or planned dimensions were used in the creation of the shop drawings.

        - Coordinate the work of this section with others effected including but not limited to: other interior and/or exterior envelope components and door hardware beyond that provided by this section

      - WARRANTY

        - Provide the Fireframes® Designer Series standard five-year manufacturer warranty.

- PRODUCTS

Adjust options in Article below to suit Project.

      - Manufacturers - FIRE RATED [DOOR ASSEMBLY] [WINDOW]

Adjust list of products in paragraph below to suit Project.

        - Glass Material:  [FireLite®] [FireLite Plus®] [FireLite® NT] [FireLite® IGU] [Fireglass®20] [Pilkington Pyrostop®] fire-rated glazing as fabricated and distributed by Technical Glass Products, 8107 Bracken Place SE, Snoqualmie, WA  98065 phone (800.426.0279) fax (425.396.8300) e-mail sales@fireglass.com, web site http://www.fireglass.com.

        - Frame System:  “Fireframes® Designer Series by TGP” fire-rated [steel] [brushed stainless steel (up to 45 minute rating)] frame system as manufactured and supplied by Technical Glass Products, 8107 Bracken Place SE, Snoqualmie, WA  98065 phone (800.426.0279) fax (425.396.8300) e-mail sales@fireglass.com web site http://www.fireglass.com.

        - Substitutions:  Substitutions for Glazing Material and Frame System not permitted.

      - performance requirements

Adjust minutes in paragraphs below to suit Project. (choose one or more as applicable)

        - Fire Rating Requirements

          - Duration -- Doors:  Capable of providing a fire rating for [20] [45] [60] [90] minutes.

            - When glazed with Pilkington Pyrostop (60-90 minutes) glazing products, doors meet the maximum transmitted temperature rise of not more than 450 degrees Fahrenheit (250 degrees Celsius) at the end of 30 minutes of the standard fire test exposure.

          - Duration-- Window Assembly:  Capable of providing a fire rating for [20] [45] [60] [90] minutes.

          - Duration--Opening Applications in fire partitions or area separation walls and corridors where opening protection is specified: Capable of providing [20] [45] [60] [90] minute rating.

        - Design Requirements:

          - Dimensions – Door and Framing:

            - Door framing face dimension:  1 15/16-inch.

            - Depth of door framing:  1 15/16-inch.

            - Door style face dimension:  3 1/8-inch.

            - Door cross rail (if applicable) face:  3 9/16-inch.

            - Depth of stile, header, sill and cross rail:  1 15/16-inch

          - Dimensions -- Window Assembly:

            - Perimeter framing face dimension:  2 3/4-inch at head, sill and jamb.

            - Horizontal and/or vertical mullions:  3 9/16-inch on the face.

            - Depth of perimeter and mullion:  1 15/16-inch.

          - Construction:  Narrow-profile, roll-formed steel architectural grade specialty fire doors.  Conventional break-shape type hollow metal steel fire-rated doors will not be considered an acceptable substitute for the Fireframes Designer Series doors specified in this section as they do not conform to the project design intent and/or aesthetic and quality standards.

            - Knock down frames are not permitted.

ASTM E330 procedure A is a test method that describes the determination of the structural performance of exterior windows, doors, skylights, and curtain walls under uniform static air pressure differences, using a test chamber. The test is intended only for evaluating the structural performance associated with the specified test specimen and not the structural performance of adjacent construction.

Member deflection is referenced from the IBC Section 24 General Requirements for Glass, article 2403.3.

        - Structural Performance

          - Design and size the system to withstand structural forces placed upon it without damage or permanent set when tested in accordance with ASTM E330 using load 1.5 times the design wind loads and of 10 seconds in duration.

          - Positive wind load: [______lbf/sq ft.][as indicated on the drawings]

          - Negative wind Load:[______lbf/sq ft.][as indicated on the drawings]

          - Member deflection: Limit deflection of the edge of the glass normal to the plane of the glass to [flexure limit of glass][1/175 of the glass edge length or ¾ inch, whichever is less][of any framing member

          - Accommodate movement between storefront and adjoining systems

Coordinate the lbf/sq ft with those required in the field test at the end of the section.

        - Air infiltration: Provide systems that allow a maximum air leakage through fixed glazed openings of 0.06 cfm/sq. ft. of area when tested per ASTM E 283 at a static air differential of [1.57] [6.24] lbf/sq ft

Coordinate the lbf/sq ft with those required in the field test at the end of the section.

        - Water Penetration

          - Under Static pressure, provide systems that do not show uncontrolled water leakage when tested according to ASTM E 331 under static pressure equal to 20 percent of positive wind-load design pressure, but not less than 6.24 lbf/sq. ft.

          - Under Dynamic pressure, provide systems that do not show uncontrolled water leakage when tested according to AAMA 501.1 under static pressure equal to 20 percent of positive wind-load design pressure, but not less than 6.24 lbf/sq. ft.

      - MATERIALS - GLASS

        - Fire Rated Glazing:  ASTM C 1036 and ASTM C 1048; composed of [ceramic] [ceramic with surface applied fire-rated film] [laminated ceramic] [insulated ceramic] [specially tempered] [wired glass] [laminated glass with intumescent interlayers] glazing material.

Adjust list of products and thicknesses below to suit Project.

        - Thickness of Glazing Material:

          - [3/16” FireLite®] [3/16” FireLite® NT] [5/16” FireLite Plus®] [FireLite® Insulated Glass Unit (IGU) as specified] FireLite products available in Premium and Standard Grade surface finishes

          - [1/4” Fireglass®20]

          - [3/4” – 1-9/16” Pilkington Pyrostop®]

          - [1/4” polished wired glass].

        - Approximate Visible Transmission:  Varies with thickness (approximate range 88 percent).

        - Logo:  Each piece of fire-rated glazing shall be labeled with a permanent logo including name of product, manufacturer, testing laboratory (UL® only), fire rating period, safety glazing standards, and date of manufacture.

        - Performance:  Glass must be rated to stop fire from either direction and must meet all testing requirements including the required hose-stream test (where fire-rating exceeds 20 minutes).

      - MATERIALS – STEEL FRAMES AND DOORS

Adjust paragraphs below to suit Project.

        - Steel Framing System including [20] [45] [60] [90]-minute rated doors, [20] [45] [60] [90]-minute rated windows.

          - Frame:  [Steel] [brushed stainless steel (up to 45 minute rating)] profiled formed tubing.

          - Fasteners:  As recommended by manufacturer

          - Glazing Accessories:  calcium silicate setting blocks.

          - Glazing Compounds:

            - FireLite®, FireLite Plus®, FireLite® NT, FireLite® IGU, Fireglass®20, or Pilkington Pyrostop®:  Approved [closed cell PVC tape], [Fibrefrax], or [pure silicone sealant]. Glaze FireLite® panels that exceed 1,393 sq. inches for 90-minute ratings with “Kerafix 2000” glazing tape supplied by manufacturer.

              - When glazed with Pilkington Pyrostop (60-90 minutes) glazing products, doors meet the maximum transmitted temperature rise of not more than 450 degrees Fahrenheit (250 degrees Celsius) at the end of 30 minutes of the standard fire test exposure.

Adjust paragraphs below to suit Project, Glazing tape comes in 45 and 90 minute tested varieties.

            - WireLite® (Wired Glass)/WireLite® NT (filmed wired glass):  FireGlaze 3000 [S45] [S90] glazing tape as distributed by Pemko Manufacturing.

      - Fabrication

        - Furnish frame assemblies pre-welded.

          - When necessary, splice frames too large for shop fabrication or shipping or to fit in available building openings.

          - Fit with suitable fasteners.

          - Knock-down frames are not permitted

        - Furnish interior frame assemblies “K-D” (or welded upon request).

          - When necessary, splice frames too large for shop fabrication or shipping or to fit in available building openings.

          - Fit with suitable fasteners.

          - Knock-down door perimeter frames are not permitted

        - Field glaze door and frame assemblies.

        - Factory prepare steel door assemblies and install all hardware.

        - Fabrication Dimensions:  Fabricate to fire-rated field dimensions.

        - Obtain approved shop drawings prior to fabrication.

      - FINISHES, GENERAL

        - Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

        - Finish frames after assembly.

        - Appearance of Finished Work:  Variations in appearance of abutting or adjacent pieces are acceptable.  Noticeable variations in the same piece are not acceptable.

- Powder coat finish systems offered and provided by Technical Glass Products are manufactured by Tiger Drylac which is a hybrid powder coating for interior applications based on a blend of epoxy-polyester. If used exteriorly contact your Technical Glass Product Representative for alternative finishes that provide an even higher standard of protection.

      - POWDERCOAT FINISHES

        - Finish after fabrication.

        - Appearance of Finished Work:	Variations in appearance of abutting or adjacent pieces are acceptable. Noticeable variations in the same piece are not acceptable.

        - Interior and Exterior Steel Finishes (Note: this finish is suitable for exterior exposed portions of the wall systems, including extruded aluminum covers).

          - Powder-Coat Finish: Polyester Super Durable powder coating which meets AAMA 2604 for chalking and fading. Apply manufacturer's standard powder coating finish system applied to factory-assembled frames before shipping, complying with manufacturer's recommended instructions for surface preparation including pretreatment, application, and minimum dry film thickness.

          - Color and Gloss: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

          - Acceptable Manufacturers:

            - Tiger Drylac

            - Additional manufacturers as approved by TGP

      - DOOR HARDWARE

        - Furnish hardware with [20] [45] [60] [90] minute fire door by the manufacturer.

        - Select hardware from door manufacturer's standard recommended and approved hardware groups as specified in Division 8 Section – Door Hardware.

        - Provide power assisted hardware for use at any door that cannot meet the opening force(s) required by code noted in Part I above.

          - High energy, power-operated doors must meet the requirements of ANSI/BHMA A156.10 and power-assisted low energy doors must comply with ANSI/BHMA A156.19

The following two hardware sets are supplied by the manufacturer and are provided here for coordination with other hardware products specified for other openings. Please contact the product representative for other options. As the doors and frames are tested as an assembly substitutions in hardware must not be allowed.

        - Operating hardware for Fireframes® Designer Series Single Inswing Doors with Mortise Lock.  Each to have the following.

|  | Item | Description | Manufacturer | Finish* |
| --- | --- | --- | --- | --- |
| 3 | Hanging Devices | Weld on Pivots | Technical Glass Products | PTM |
| 1 | Lever Trim | Narrow Escutcheon Lever Trim Set DSR2NNOL# | Securitech | 630 |
| 1 | Mortise Lock | Mortise lock with panic function | WSS | 630 |
| 1 | Cylinder | European Profile Schlage C Keyway | Technical Glass Products | 626 |
| 1 | Closer | 4040XP Surface Mounted | LCN | 689 |
| 1 | Auto door Bottom | 420APKL Smoke Seal | Pemko | MA |
| 1 | Weather Seal | Perimeter Gasket | Technical Glass Products |  |
|  | Balance of hardware by others |  |  |  |

        - Operating hardware for Fireframes® Designer Series Single Outswing Doors with Mortise Lock.  Each to have the following.

|  | Item | Description | Manufacturer | Finish* |
| --- | --- | --- | --- | --- |
| 3 | Hanging Devices | Weld on Pivots | Technical Glass Products | PTM |
| 1 | Lever Trim | LX Series Control Trim Lever Set DSR1GNOL# | Securitech | 630 |
| 1 | Mortise Lock | Mortise lock with panic function | WSS | 630 |
| 1 | Cylinder | ANSI Mortise Schlage C Keyway | Technical Glass Products | 626 |
| 1 | Closer | 4040XP Surface Mounted | LCN | 689 |
| 1 | Auto door Bottom | 420APKL Smoke Seal | Pemko | MA |
| 1 | Weather Seal | Perimeter Gasket | Technical Glass Products |  |
|  | Balance of hardware by others |  |  |  |

        - Operating hardware for Fireframes® Designer Series Single Outswing Doors with Exit Device. Each to have the following.

|  | Item | Description | Manufacturer | Finish* |
| --- | --- | --- | --- | --- |
| 3 | Hanging Devices | Weld on Pivots | Technical Glass Products | PTM |
| 1 | Exit Device | 35A-F Rim | Von Duprin | 626 |
| 1 | Lever Trim | 360L | Von Duprin | 626 |
| 1 | Cylinder | ANSI Mortise Schlage C Keyway | Technical Glass Products | 626 |
| 1 | Closer | 4040XP Surface Mounted | LCN | 689 |
| 1 | Auto door Bottom | 420APKL Smoke Seal | Pemko | MA |
| 1 | Weather Seal | Perimeter Gasket | Technical Glass Products |  |
|  | Balance of hardware by others |  |  |  |

        - Operating hardware for Designer Series Active-Fixed Inswing Pair of Doors with Mortise Lock. Each pair to have the following.

|  | Item | Description | Manufacturer | Finish* |
| --- | --- | --- | --- | --- |
| 6 | Hanging Devices | Weld on Pivots | Technical Glass Products | PTM |
| 1 | Lever Trim | Narrow Escutcheon Lever Trim Set DSR2NNOL# | Securitech | 630 |
| 1 | Mortise Lock | Mortise lock with panic function | WSS | 630 |
| 1 | Cylinder | European Profile Schlage C Keyway | Technical Glass Products | 626 |
| 2 | Cylinder Rosettes | 17 1757 00010 | FSB | 630 |
| 2 | Closers | 4040XP Surface Mounted | LCN | 689 |
| 1 | Coordinator | 3092 | Trimco | 622 |
| 1 | Flush Bolt Set | Automatic or Semi-Automatic Flush bolt with dust proof recessed strike | Trimco | 626 |
| 2 | Auto door Bottoms | 420APKL Smoke Seal | Pemko | MA |
| 1 | Weather Seal | Perimeter Gasket | Technical Glass Products |  |
|  | Balance of hardware by others |  |  |  |

        - Operating hardware for Fireframes® Designer Series Active-Fixed Outswing Pair of Doors with Mortise Lock. Each pair to have the following.

|  | Item | Description | Manufacturer | Finish* |
| --- | --- | --- | --- | --- |
| 6 | Hanging Devices | Weld on Pivots | Technical Glass Products | PTM |
| 1 | Lever Trim | LX Series Control Trim Lever Set DSR1GNOL# | Securitech | 630 |
| 1 | Mortise Lock | Mortise lock with panic function | WSS | 630 |
| 1 | Cylinder | ANSI Mortise Schlage C Keyway | Technical Glass Products | 626 |
| 2 | Cylinder Rosettes | 17 1757 00010 | FSB | 630 |
| 2 | Closers | 4040XP Surface Mounted | LCN | 689 |
| 1 | Coordinator | 3092 | Trimco | 622 |
| 1 | Flush Bolt Set | Automatic or Semi-Automatic Flush bolt with dust proof recessed strike | Trimco | 626 |
| 2 | Auto door Bottoms | 420APKL Smoke Seal | Pemko | MA |
| 1 | Weather Seal | Perimeter Gasket | Technical Glass Products |  |
|  | Balance of hardware by others |  |  |  |

        - Operating hardware for Fireframes® Designer Series Active-Fixed Pair of Doors Outswing with Exit Device. Each pair to have the following.

|  | Item | Description | Manufacturer | Finish* |
| --- | --- | --- | --- | --- |
| 6 | Hanging Devices | Weld on Pivots | Technical Glass Products | PTM |
| 1 | Exit Device | 3547A-F Concealed Vertical Rod | Von Duprin | 626 |
| 1 | Lever Trim | 360L | Von Duprin | 626 |
| 1 | Cylinder | ANSI Mortise Schlage C Keyway | Technical Glass Products | 626 |
| 2 | Closers | TS93 Surface Mounted | Dorma | 689 |
| 1 | Coordinator | GSR | Dorma | 689 |
| 1 | Flush Bolt Set | Automatic or Semi-Automatic Flush bolt with dust proof recessed strike | Trimco | 626 |
| 2 | Auto door Bottoms | 420APKL Smoke Seal | Pemko | MA |
| 1 | Weather Seal | Perimeter Gasket | Technical Glass Products |  |
|  | Balance of hardware by others |  |  |  |

        - Operating hardware for Fireframes® Designer Series Active-Active Pair of Doors Outswing with Exit Device. Each pair to have the following.

|  | Item | Description | Manufacturer | Finish* |
| --- | --- | --- | --- | --- |
| 6 | Hanging Devices | Weld on Pivots | Technical Glass Products | PTM |
| 2 | Exit Device | 3547A-F Concealed | Von Duprin | 626 |
| 2 | Lever Trim | 360L | Von Duprin | 626 |
| 1 | Cylinder | ANSI Mortise Schlage C Keyway | Technical Glass Products | 626 |
| 2 | Closers | 4040XP Surface Mounted | LCN | 689 |
| 2 | Auto door Bottoms | 420APKL Smoke Seal | Pemko | MA |
| 1 | Auxiliary Fire Latch | Used with exit device with no bottom rod | Technical Glass Products | 630 |
| 1 | Weather Seal | Perimeter Gasket | Technical Glass Products |  |
|  | Balance of hardware by others |  |  |  |

* FINISH LEGEND:

PTM	Painted to match frame

MA	Mill Finish Aluminum

689	Aluminum Paint

630	Satin Stainless Steel

626	Satin Chrome Plated

      - ACCESSORY MATERIALS

        - Bituminous Paint:  Cold-applied, asphalt-mastic paint complying with SSPC-Paint 12 requirements except containing no asbestos; formulated for [30-mil] [0.762-mm] thickness per coat.

- EXECUTION

      - EXAMINATION

        - Examine substrates and members to which the work of this section attaches or adjoins prior to frame installation.

        - Provide openings plumb, square and within allowable tolerances.

          - Provide 3/8 inch shim space at all walls

        - Notify Architect of any conditions which jeopardize the integrity of the proposed fire wall / door system.

        - Do not proceed until such conditions are corrected.

      - INSTALLATION

        - See Fireframes Designer Series Installation Manual

      - REPAIR AND TOUCH UP

        - Limited to minor repair of small scratches. Use only manufacturer’s recommended products.

          - Such repairs shall match original finish for quality or material and view.

        - Remove and replace glass that is broken, chipped, cracked, abraded, or damaged.

      - ADJUSTING

        - Adjust door function and hardware for smooth operation. Coordinate with other hardware suppliers for function and use of any other attached hardware.

      - PROTECTION AND CLEANING

        - Protect glass from damage immediately after installation by attaching crossed streamers to framing held away from glass.  Do not apply markers to glass surface.  Remove nonpermanent labels, and clean surfaces.

          - Do not clean with astringent cleaners. Use a clean “grit free” cloth and a small amount of mild soap and water or mild detergent.

          - Do not use any of the following:

            - Steam jets

            - Abrasives

            - Strong acidic or alkaline detergents, or surface-reactive agents

            - Detergents not recommended in writing by the manufacturer

            - Do not use any detergent above 77 degrees F

            - Organic solvents including but not limited to those containing ester, ketones, alcohols, aromatic compounds, glycol ether, or halogenated hydrocarbons.

            - Metal or hard parts of cleaning equipment must not touch the glass surface

        - Protect glass from contact with contaminating substances resulting from construction operations, including weld splatter.  If, despite such protection, contaminating substances do come into contact with glass, remove them immediately as recommended by glass manufacturer.

Modify paragraph below to suit Project.

        - Wash glass on both exposed surfaces in each area of Project not more than four days before date scheduled for inspections that establish date of Substantial Completion.  Wash glass as recommended by glass manufacturer.

end of section