Technical Glass Products has included notes in this specification to assist you in tailoring the content to your project.  These comments will appear on your screen in blue.  To hide them and view only the specification, do the following:  Click on “Tools” on your Microsoft Word toolbar.  Under Tools, select “Options.” On the “View” tab, under “Formatting Marks,” remove the check mark from the “Hidden Text” box.  Then click “OK.”  All blue text will then be hidden.  For assistance, call Technical Glass Products at 1-800-426-0279.

This guide specification is a supplier-specific proprietary product specification using the proprietary method of specifying applicable to project specifications and master guide specifications. Optional text is indicated by brackets []; delete optional text in final copy of specification.

This Section specifies “Pilkington Pyrostop® fire-rated, impact safety-rated transparent wall panels supplied by Technical Glass Products further described in Part 2 – Products.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

SECTION 08 88 13 - FIRE-RATED, Bullet Resistant FIREGLASS® laminated to forced entry resistant SCHOOL GUARD GLASS®

- GENERAL

      - SUMMARY

        - Section Includes:

          - Fire-rated glazing materials carrying bullet resistant and forced entry ratings installed as vision lights in fire-rated doors.

          - Fire-rated glazing materials carrying bullet resistant and forced entry ratings installed as [sidelites] [transoms] [borrowed lites] in fire-rated frames and [wall applications].

Verify that Section titles referenced below are correct for this Project's Specifications; Section titles may have changed. Revise Section number and title below to suit project requirements, specification practices and section content. Refer to CSI MasterFormat for other section numbers and titles.

        - Related Sections include the following:

          - Section 08 11 00 “Metal Doors and Frames” for vision panels in interior doors and interior vision panel (borrowed lites) frames.

          - Section 08 14 16 “Flush Wood Doors” for vision panels in interior doors.

          - [Section 09 21 00 “Gypsum Board Assemblies” for gypsum board and metal stud framed area separation partition walls.]

      - references

- Adjust lists below to suit Project. Coordinate with Part 2

        - American Society for Testing and Materials (ASTM):

          - ASTM E 119:  Fire Tests of Building Construction and Materials.

          - ASTM F1233: Standard Test Method for Security Glazing Materials and Systems

          - ASTM C1036: Standard Specification Flat Glass

          - ASTM C1172:  Standard Specification for Laminated Architectural Flat Glass

        - American National Standards Institute (ANSI):

          - ANSI Z97.1:  Standard for Safety Glazing Materials Used in Buildings

        - Consumer Product Safety Commission (CPSC):

          - CPSC 16 CFR 1201:  Safety Standard for Architectural Glazing Materials

        - Glass Association of North America (GANA):

          - GANA – Glazing Manual.

          - FGMA – Sealant Manual.

        - National Fire Protection Association (NFPA):

          - NFPA 80:  Fire Doors and Windows.

          - NFPA 251: Standard Methods of Tests of Fire Endurance of Building Construction and Materials

          - NFPA 252: Fire Tests of Door Assemblies

          - NFPA 257: Fire Tests of Window Assemblies.

        - Underwriters Laboratories, Inc. (UL):

          - UL 9:  Fire Tests of Window Assemblies.

          - UL 10B:  Fire Tests of Door Assemblies.

          - UL 10C:  Positive Pressure Fire Tests of Door Assemblies.

          - UL 263:  Fire tests of Building Construction and Materials

          - UL 752:  Standard for Bullet-Resisting Equipment

Following are Canadian Standards

        - Standard Council of Canada:

          - CAN/ULC-S101 Standard Test of Fire Endurance Tests of Building Construction and Materials

          - CAN/ULC-S104 Standard Method of Fire Tests of Door Assemblies

          - CAN/ULC-S106 Standard Method of Fire Tests of Window and Glass Block Assemblies

        - H.P. White Laboratory, Inc. (HPW)

          - HPW 5-aa1: Standards for Retrofitting and Reinforcing of Standard Commercial Entry Systems, Windows and Glazing

      - PERFORMANCE REQUIREMENTS

        - Fire-rated, clear and wireless glazing material for use in locations such as doors, sidelites, transoms, borrowed lites, and wall applications with fire rating requirements ranging from 45 minutes to 90 minutes with required hose stream test; for use in interior and exterior applications.

        - Provides protection by reducing the radiant and conductive heat transfer

        - Security Glazing: Security glass and surrounding frames shall demonstrate the ability, through independent third party testing, to provide the following attributes:

- Products tested shall be tested in full size, actual doors and framing members usable in a commercial setting, as applicable to project requirements, with security glazing installed as prescribed by the security glazing manufacturer. Testing shall not be done in framing other than what is specified in regards to quality or manufacturer as stated in the Contract Documents.

- Glass bite during testing shall be no more than the allowable glass bite in the specified door or framing system for this project.

- The security glass shall resist attack for a minimum of 6 minutes or greater to meet the desired level of protection required by the owner.

- Attack duration shall be continuous.  Breaks between testing phases shall not be counted or timed for total duration.

- Security glass will be integrated into a framing system in such a way that the frame and glass are able to withstand a constant attack for 6 minutes.

- Attack resistance shall mean the security glazing is subjected to the following without failure:

- Withstand a minimum of 5 shots from a military style assault rifle with a minimum caliber of 7.62mm.

- Withstand a minimum of abuse as applied by a single assailant at full force and including strikes with feet, bricks, hammers, baseball bats, and sledgehammers without stoppage for 6 or 12 minutes.

- Failure is defined as a tear in the security glass large enough to allow an object 4-inches in diameter or more to pass through or separation made between the glass and surrounding door frame, storefront or curtain wall framing materials.

- Test reports from a recognized independent testing company shall show testing means and methodology consistent or similar to the 5-aa1 assault test.

      - SUBMITTALS

- Note:  Specify submittal requirements for fire-rated doors and fire-rated frames, including glass stops in the appropriate Sections.

        - Comply with requirements of Section 01 33 00<Insert Section #>.

        - Product data:  Submit manufacturer’s technical data for each glazing material required, including installation and maintenance instructions.

        - Certificates of compliance from glass and glazing materials manufacturers attesting that glass and glazing materials furnished for project comply with requirements. Separate certification will not be required for glazing materials bearing manufacturer’s permanent label designating type and thickness of glass, provided labels represent a quality control program involving a recognized certification agency or independent testing laboratory acceptable to authority having jurisdiction.

        - Product Test Listings:  From UL indicating fire-rated glass complies with requirements, based on comprehensive testing of current product.

        - Samples:  Submit, for verification purposes, approx. 8-inch by 10-inch sample for each type of glass indicated.

      - QUALITY ASSURANCE

        - Glazing Standards:  FGMA Glazing Manual and Sealant Manual.

        - Fire Resistance Rated Glass:  Each lite shall bear permanent, nonremovable label of UL certifying it for use in tested and rated fire resistive assemblies.

      - delivery, storage, and handling

        - Deliver, store, and handle materials under provisions of Section 01 60 00<Insert Section #>.

        - Deliver materials to specified destination in manufacturer or distributor’s packaging, undamaged, complete with installation instructions.

        - Fireglass® must not be exposed outside the range -40 degrees F to 120 degrees F (-40 degree C to +50 degrees C) during storage and transportation.

        - Store off ground, under cover, protected from weather and construction activities.

        - Do not expose the non-PVB side of glass to UV light.

        - Store sheets of glass vertically.  DO NOT lean.

      - warranty

        - Provide manufacturer's standard warranty.

- PRODUCTS

      - fire-rated glazing MATERIALS

        - Manufacturer:  Fireglass® as manufactured by the Pilkington Group and Laminated Technologies Inc, 8107 Bracken Place SE, Snoqualmie, WA  98065, voice 1-800-426-0279, fax 1-800-451-9857, e-mail sales@fireglass.com, Web site  www.fireglass.com. and Laminated Technologies Inc. 14 Federico Drive, Pittsfield, MA 01201, voice 413-637-5001, fax 413-637-5004, website www.ltisg.com

        - Composition:  Composed of multiple sheets of “Optiwhite” high visible light transmission glass laminated with an intumescent interlayer. [Most configurations are available with a translucent interlayer for added obscurity and privacy.]

        - Properties:

- 1.     Thickness: For Interior Use:  [3/4”, #45-200], [7/8”, #60-101], [1-1/16” #60-201], [1-7/16, #90-102].

            - For Exterior Use, Single Glazing:  [3/4”, #45-200], [1-1/16”, #60-201].

            - For Exterior Use, Insulated Glass Unit:  [1-5/16”, #45-260], [1-5/16”, #45-360], [1-5/8”, #60-261], [1-5/8”, #60-361]

          - Weight:  Varies with thickness (approximate range 9 to 22 lbs./sq. ft.).

          - Approximate Visible Transmission:  Varies with thickness (approximate range 88 to 75 percent).

          - Fire-rating:  Up to 90 minutes.

          - Impact Safety Resistance:  ANSI Z97.1 and CPSC 16CFR1201 (Cat. I and II).

          - STC Rating:  Up to 46 dB.

- Note:  60 minute, 90 minute and 2 hour glass is made with OPTIWHITE high visible light transmission glass.

          - Exterior Grade:  PVB layer on exterior surface.

        - Permanently label each piece of Fireglass® with the appropriate marking.

        - Fire Rating – 60 Minutes and Greater:  Fire rating classified and labeled by UL for fire rating scheduled at opening locations on drawings, when tested in accordance with ASTM E 119 and UL 263.

        - Substitutions:  No substitutions allowed.

      - security glazing materials

        - Manufacturer:  School Guard Glass® as manufactured by Laminated Technologies Inc. 14 Federico Drive, Pittsfield, MA 01201, voice 413-637-5001, fax 413-637-5004, website www.ltisg.com

        - Composition:

          - [SG5™ is a laminated glass product consisting of outer layers of glass with a custom security, heat strengthened, chemically bonded core.]

        - Properties:

          - Thickness:  [ ¼”-3/8”, SG5]

          - Weight:  [4.1 lbs/ft2, SG5]

        - Permanently label each piece of [SG5] with the appropriate marking.

        - Substitutions:  No substitutions allowed.

      - GLAZING COMPOUND FOR FIRE-RATED GLAziNG MATERIALS

        - Glazing Tape:  Closed cell polyvinyl chloride foam, coiled on release paper over adhesive on two sides, maximum water absorption by volume of 2 percent, designed for compression of 25 percent to effect an air and vapor seal.

        - Setting Blocks:  Hardwood or calcium silicate; glass width by 4 inches by 3/16 inch thick.

        - Spacers:  Neoprene or other resilient blocks of 40 to 50 Shore A durometer hardness, adhesive-backed on one face only, tested for compatibility with specified glazing compound.

        - Cleaners, Primers, and Sealers:  Type recommended by manufacturer of glass and gaskets.

      - FABRICATION

        - Fabricate glass and other glazing products in sizes required to glaze openings indicated for Project, with edge and face clearances, edge and surface conditions, and bite complying with recommendations of product manufacturer and referenced glazing standard as required to comply with system performance requirements.

- EXECUTION

      - EXAMINATION

        - Examine glass framing, with glazier present, for compliance with the following:

          - Manufacturing and installation tolerances, including those for size, squareness, offsets at corners.

          - Minimum required face or edge clearances.

          - Observable edge damage or face imperfections.

        - Do not proceed with glazing until unsatisfactory conditions have been corrected.

        - Clean glazing channels and other framing members receiving glass immediately before glazing.  Remove coatings that are not firmly bonded to substrates.

      - INSTALLATION (GLAZING)

        - Comply with referenced GANA standards and instructions of manufacturers of glass, glazing sealants, and glazing compounds.

        - Protect glass from edge damage during handling and installation.  Inspect glass during installation and discard pieces with edge damage that could affect glass performance.

        - Cut glazing tape to length and set against permanent stops, flush with sight lines to fit openings exactly, with stretch allowance during installation.

        - Place setting blocks located at quarter points of glass with edge block no more than 6-inches from corners.

        - Glaze vertically into labeled fire-rated metal frames or partition walls with the same fire rating as glass and push against tape for full contact at perimeter of pane or unit.

        - Place glazing tape on free perimeter of glazing in same manner described above.

        - Do not remove protective edge tape.

        - Install removable stop and secure without displacement of tape.

        - Do not pressure glaze.

        - Glaze exterior openings with PVB layer toward the exterior of the building.

        - Knife trim protruding tape.

        - Apply cap bead of silicone sealant along void between the stop and the glazing, to uniform line, with bevel to form watershed away from glass.  Tool or wipe sealant surface smooth.

        - Provide minimum ¼” inch edge clearance.

        - Install in vision panels in fire-rated doors to requirements of NFPA 80.

        - Install so that appropriate UL and Fireglass® markings remain permanently visible.

        - Install glazing materials in accordance with the manufacturers printed instructions

      - PROTECTION AND CLEANING

        - Protect glass from contact with contaminating substances resulting from construction operations.  Remove any such substances by method approved by glass manufacturer.

        - Wash glass on both faces not more than four days prior to date scheduled for inspections intended to establish date of substantial completion.  Wash glass by method recommended by glass manufacturer.

- NOTE:  SEE GLAZING SCHEDULE ON FOLLOWING TWO PAGES

      - GLAZING SCHEDULE

        - SCHOOL GUARD GLASS ASTM F1233 AND HPW 5-aa1 (SG5):

| - Fire Rating | - Manufacturer Designation | - Supply Form | - Thickness | - Weight Approx. | - Assembly | - Max. Exposed Area | - Max. Width Of Exposed Glazing | - or |  | - Max. Height Of Exposed Glazing |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| - 45 min. | - 45-200 | - Single Glazing | - 1.25” (32 mm) | 13.82 lb / ft2 (67.46 kg / m2) | - Other than doors Door | 4,500 in2 (2.90 m2) 3,724 in2 (2.40 m2) | 95-1/4" (2.42 m) 41-5/8" (1.06 m) |  |  | 95-1/4" (2.42 m) 89-3/4" (2.28 m) |
| - 60 min. | - 60-101^ | - Single Glazing | 1.41" (36 mm) | 15.46 lbs/ft² - (75.46 kg/m2) | - Other than doors Door | 5,616 in2 (3.62 m2) 3,724 in2 (2.40 m2) | 96" (2.44 m) 41-5/8" (1.06 m) |  |  | 96" (2.44 m) 89-3/4" (2.28 m) |
| - 60 min. | - 60-201+ | - Single Glazing | 1.57" (40 mm) | 17.50 lbs/ft² - (85.46 kg/m2) | - Other than doors - Door | 7,442 in2 (4.80 m2) 3,724 in2 (2.40 m2) | 96" (2.44 m) 41-5/8" (1.06 m) |  |  | 118-1/8" (3.00 m) 89-3/4" (2.28 m) |
| - 90 min. | - 90-102^ | - Single Glazing | 1.96" (50 mm) | 22.21 lbs/ft² - (108.46 kg/m2) | - Other than doors Door | 3,724 in2 (2.40 m2) 3,724 in2 (2.40 m2) | 96" (2.44 m) 41-5/8" (1.06 m) |  |  | 96" (2.44 m) 89-3/4" (2.28 m) |

Note: Both Fireglass® and School Guard Glass® have a ± 1/16” tolerance giving an overall thickness tolerance of ± 1/8”

+ Available with a translucent interlayer

- ^ Interior use only

- B.  UL-752 BULLET RESISTANCE GLASS

| - UL-752 Bullet Resistance Rating | - Fire-Rating | - Fireglass Designation | - Supply Form | - Nominal - Thickness | - Weight Approx. | - Assembly | - Max. Exposed Area | - Max. Width Of Exposed Glazing | - or | - Max. Height Of Exposed Glazing |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| - Level I | - 60 min. | - 60-201 (with film*+^) | Single Glazing | 1-1/16" (27 mm) | 12.90 lbs/ft2 (63.00 kg/m2) | Other than doors Doors | 7,442 in2 (4.80 m2) - 3,724 in2 (2.40 m2) | 96" (2.44 m) - 41–5/8" (1.06 m) |  | 118–1/8" (3.00 m) - 89–3/4" (2.28 m) |
| - Level II | - 120 min. | - 120-202+^ | I.G. Units | 2-7/16" (62 mm) | 25.81 lbs/ft2 (126.00 kg/m2) | Other than doors | 3,724 in2 (2.40 m2) | 111" (2.81 m) |  | 111" - (2.81 m) |
| - Level III | - 120 min. | - 120-201 (with film*+^) | I.G. Units | 2-7/16" (62 mm) | 25.81 lbs/ft2 (126.00 kg/m2) | Other than doors | 3,724 in2 (2.40 m2) | 111" (2.81 m) |  | 111" - (2.81 m) |
| - Level II | - 120 min. | - 120-202 (with film*) | Single Glazing | 1-9/16" (41 mm) | 18.64 lbs/ft2 (91.00 kg/m2) | - Other than doors Door | 3,724 in2 (2.40 m2) - 3,724 in2 (2.40 m2) | 111" (2.81 m) - 41–5/8" (1.06 m) |  | 111" (2.81 m) - 89–3/4" (2.28 m) |

*For filmed products, one dimension of the glass cannot exceed 60" (1.52 m)

+ Available with a translucent interlayer

^ Interior use only