Technical Glass Products has included notes in this specification to assist you in tailoring the content to your project.  These comments will appear on your screen in blue.  To hide them and view only the specification, do the following:  Click on “Tools” on your Microsoft Word toolbar.  Under Tools, select “Options.” On the “View” tab, under “Formatting Marks,” remove the check mark from the “Hidden Text” box.  Then click “OK.”  All blue text will then be hidden.  For assistance, call Technical Glass Products at 1-800-426-0279.

This guide specification is a supplier-specific proprietary product specification using the proprietary method of specifying applicable to project specifications and master guide specifications. Optional text is indicated by brackets []; delete optional text in final copy of specification.

This Section specifies “FireLite Plus® WS” fire-rated, impact safety-rated laminated glass ceramic supplied by Technical Glass Products as further described in Part 2 – Products.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

SECTION 08 88 13 – FIRE-RATED GLASS - FIRELITE PLUS® WS

- GENERAL

      - SUMMARY

        - Section Includes:

          - Fire-rated glazing materials installed as windows in fire separations intended for use with Tyco Model WS Specific Application Window Sprinklers.

Verify that Section titles referenced below are correct for this Project's Specifications; Section titles may have changed. Revise Section number and title below to suit project requirements, specification practices and section content. Refer to CSI MasterFormat for other section numbers and titles.

        - Related Sections include the following:

          - Section 06 40 00 “Architectural Woodwork” for wood frames for doors, sidelights, transoms, borrowed lights.

          - Section 08 11 00 “Metal Doors and Frames” for vision panels in interior doors and interior vision panel (borrowed lites) frames.

          - Section 08 14 16 “Flush Wood Doors” for vision panels in interior doors.

          - Section 08 14 33 “Stile and Rail Wood Doors” for vision panels in interior doors.

          - Section 08 51 23 “Steel Windows.”

          - 21 13 13 Wet-Pipe Sprinkler Systems

          - 21 13 19 Preaction Sprinkler Systems

          - 21 13 23 Combined Dry-Pipe and Preaction Sprinkler Systems

          - 21 13 26 Deluge Fire-Suppression Sprinkler Systems

      - references

Adjust lists below to suit Project.

          - ASTM E2010-01:  Standard Test Method for Positive Pressure Fire Tests of Window Assemblies.

        - American National Standards Institute (ANSI):

          - ANSI Z97.1:  Standard for Safety Glazing Materials Used in Buildings

        - Consumer Product Safety Commission (CPSC):

          - CPSC 16 CFR 1201:  Safety Standard for Architectural Glazing Materials

        - Glass Association of North America (GANA):

          - GANA – Glazing Manual.

          - FGMA – Sealant Manual.

        - National Fire Protection Association (NFPA):

          - NFPA 80:  Fire Doors and Windows.

          - NFPA 252 – Fire Tests of Door Assemblies.

          - NFPA 257 – Fire Tests of Window Assemblies.

        - Underwriters Laboratories, Inc. (UL):

          - UL 9 – Fire Tests of Window Assemblies.

          - UL 10B – Fire Tests of Door Assemblies.

          - UL 10C – Positive Pressure Fire Tests of Door Assemblies.

Following are Canadian Standards:

        - Standard Council of Canada:

          - CAN/ULC-S101:  Standard Methods of Fire Endurance Tests.

          - CAN/ULC-S104 Fire Tests of Door Assemblies.

          - CAN/ULC-S106: Fire Tests of Window Assemblies.

        - <Insert building code name used by authority having jurisdiction>.

      - SUBMITTALS

Specify submittal requirements for fire-rated doors and fire-rated frames, including glass stops in the appropriate Sections.

        - Comply with requirements of Section 01 33 00<Insert Section #>.

        - Product Data:  Submit manufacturer’s technical data for each glazing material required, including installation and maintenance instructions.

        - Certificates of compliance from glass and glazing materials manufacturers attesting that glass and glazing materials furnished for project comply with requirements. Separate certification will not be required for glazing materials bearing manufacturer’s permanent label designating type and thickness of glass, provided labels represent a quality control program involving a recognized certification agency or independent testing laboratory acceptable to authority having jurisdiction.

        - Letter or notation from Authority Having Jurisdiction that the specified assembly is acceptable for the use intended.

        - Product Test Listings:

          - From UL indicating fire-rated glass complies with requirements, based on comprehensive testing of current product.

          - ICC-ES Evaluation Report: provide ICC Evaluation Service report for approved system.

        - Samples:  Submit, for verification purposes, approx. 8-inch by 10-inch sample for each type of glass indicated.

      - QUALITY ASSURANCE

        - Glazing Standards:  FGMA Glazing Manual and Sealant Manual.

        - Fire Protective Rated Glass:  Each lite shall bear permanent, nonremovable label of UL certifying it for use in tested and rated fire protective assemblies.

        - Fire Protective Glazing Products for Door Assemblies:  Products identical to those tested per UL 10B, classified and listed by UL.

      - delivery, storage, and handling

        - Deliver, store, and handle materials under provisions of Section 01 60 00<Insert Section #>.

        - Deliver materials to specified destination in manufacturer or distributor’s packaging, undamaged, complete with installation instructions.

        - Store off ground, under cover, protected from weather and construction activities.

      - WARRANTY

        - Provide FireLite Plus® standard five-year manufacturer warranty.

- PRODUCTS

      - fire-rated glazing MATERIALS

        - Manufacturer: FireLite Plus® WS as manufactured by Nippon Electric Glass Company, Ltd., and distributed by Technical Glass Products, 8107 Bracken Place SE, Snoqualmie, WA  98065, phone (800.426.0279) fax (425.396.8300), e-mail sales@fireglass.com, web site www.fireglass.com.

        - Properties:

- Note:  Figures are for FireLite Plus® Premium Grade. Figures will differ slightly for FireLite Plus® Standard Grade.

- FireLite Plus® Standard Grade is comparable to alternative fire-rated ceramics that are marketed as having a “Premium” finish.  If a Premium finish is desired, ensure that only polished products are allowed such as FireLite Plus® Premium Grade.  FireLite Plus® Premium Grade is ground and polished on both sides to eliminate any surface distortion.  FireLite products now feature ultraHD® Technology to reduce perceptible color and improve surface quality.

          - Thickness:  5/16 inch [8 mm] overall.

          - Weight:  4 lbs./sq. ft.

          - Approximate Visible Transmission:  85 percent.

          - Approximate Visible Reflection:  9 percent.

          - Fire-rating: 2 hours

          - Impact Safety Resistance:  ANSI Z97.1 and CPSC 16CFR1201 (Cat. I and II).

          - STC Rating:  Approximately 38 dB.

          - Surface Finish:

            - Premium Grade-Ground and polished on both sides

            - Standard Grade-Comparable surface finish to alternative fire-rated ceramic products marketed as “Premium”

          - Positive Pressure Test:  UL 10C; passes.

        - Maximum allowable per piece glass size based on system approvals:

          - Premium:  36 inches by 96 inches.

          - Standard:  36 inches by 96 inches.

        - Labeling:  Permanently label each piece of FireLite Plus® WS with the FireLite Plus® logo, UL logo and when using FireLite Plus® alone and not part of the FireLite Plus® WS system, and for sizes that exceed the listing label with the FireLite Plus® label only (as approved by the local authority having jurisdiction).

        - Fire Rating:  Fire rating listed and labeled by UL for fire rating scheduled at opening locations on drawings, when tested in accordance with [ASTM E2010-01] [ULC Standards CAN4 S-104 and CAN4 S-106] [NPFA 252 and NFPA 257] [UL 9, UL 10B and UL 10C].

        - Substitutions:  No substitutions allowed.

      - PERFORMANCE REQUIREMENTS

        - Fire-rated glass ceramic laminated clear and wireless glazing material for use in impact safety-rated fire separations such as windows and sidelites intended for use with TYCO Model WS Specific Application Window Sprinklers.

        - Passes positive pressure test standards UL10C.

This product is not a barrier to radiant heat. This product does not meet test standards ASTM E 119 or UL 263. If your jurisdiction requires a “barrier to heat” product, please contact Technical Glass Products regarding Pilkington Pyrostop®.

May be lightly sandblasted/etched or beveled on one side without affecting fire rating.

      - GLAZING COMPOUND FOR FIRE-RATED GLAZING MATERIALS

Select one the following: glazing tape, or glazing compound or silicone sealant.

        - Glazing Tape:  Closed cell polyvinyl chloride (PVC) foam, coiled on release paper over adhesive on two sides, maximum water absorption by volume of 2 percent.

        - [Glazing Compound: DAP 33 putty.]

        - [Silicone Sealant:  One-part neutral curing silicone, medium modulus sealant, Type S; Grade NS; Class 25 with additional movement capability of 50 percent in both extension and compression (total 100 percent); Use (Exposure) NT; Uses (Substrates) G, A, and O as applicable. Available Products:

          - Dow Corning 795 - Dow Corning Corp.

          - Silglaze-II 2800 - General Electric Co.

          - Spectrem 2 - Tremco Inc.]

        - Setting Blocks:  Neoprene, EPDM, or silicone; tested for compatibility with glazing compound; of 70 to 90 Shore A hardness.

        - Cleaners, Primers, and Sealers:  Type recommended by manufacturer of glass and gaskets.

      - FABRICATION

        - Fabricate glass and other glazing products in sizes required to glaze openings indicated for Project, with edge and face clearances, edge and surface conditions, and bite complying with recommendations of product manufacturer and referenced glazing standard as required to comply with system performance requirements.

- EXECUTION

      - EXAMINATION

        - Examine glass framing, with glazier present, for compliance with the following:

          - Manufacturing and installation tolerances, including those for size, squareness, offsets at corners.

          - Minimum required face or edge clearances.

          - Observable edge damage or face imperfections.

          - Verify rough-in locations for TYCO Model WS Specific Application Window Sprinkler

        - Do not proceed with glazing until unsatisfactory conditions have been corrected.

        - Clean glazing channels and other framing members receiving glass immediately before glazing.  Remove coatings that are not firmly bonded to substrates.

      - INSTALLATION (GLAZING)

        - Comply with referenced FGMA standards and instructions of manufacturers of glass, glazing sealants, and glazing compounds.

        - Protect glass from edge damage during handling and installation.  Inspect glass during installation and discard pieces with edge damage that could affect glass performance.

        - Set units of glass in each series with uniformity of pattern, draw, bow, and similar characteristics.

        - Cut glazing tape to length and set against permanent stops, flush with sight lines to fit openings exactly, with stretch allowance during installation.

        - Place setting blocks located at quarter points of glass with edge block no more than 6 inches from corners.

        - Glaze vertically into labeled fire-rated metal frames or partition walls with same fire rating as glass and push against tape for full contact at perimeter of pane or unit.

        - Place glazing tape on free perimeter of glazing in same manner described above.

        - Install removable stop and secure without displacement of tape.

        - [Use specified glazing compound, without adulteration; bed glazing material in glazing compound; entirely fill all recess and spaces. Provide visible glazing compound with smooth and straight edges.]

        - Install in vision panels in fire-rated doors to requirements of NFPA 80.

        - Install so that appropriate [UL] [FireLite Plus®] markings remain permanently visible.

      - PROTECTION AND CLEANING

        - Protect glass from contact with contaminating substances resulting from construction operations.  Remove any such substances by method approved by glass manufacturer.

        - Wash glass on both faces not more than four days prior to date scheduled for inspections intended to establish date of substantial completion.  Wash glass by method recommended by glass manufacturer.

Special approval is required from the local authority having jurisdiction when using FireLite® Plus in applications requiring a non-standard rating or sizes larger than those scheduled above and in paragraph 2.1, C. In such cases FireLite® Plus will be furnished with a FireLite® Plus label only.

END OF SECTION