Technical Glass Products has included notes in this specification to assist you in tailoring the content to your project.  These comments will appear on your screen in blue.  To hide them and view only the specification, do the following:

Click the “Office” button and then click the word “Options” OR select the “File” and then click “Options”.   Click “Display” at the left of the dialog box.  Remove the check mark from the “Hidden Text” box.  Then click “OK.”  All blue text will then be hidden.

This document is designed for use by a qualified construction specifier. Proper modifications are required to tailor this specification to your project needs.  Optional text is placed between brackets “[ ].”  Blank underlines “__” represent areas you need to fill in with your project specific information. For assistance, call Technical Glass Products at 1-800-426-0279.

This guide specification is a supplier-specific proprietary product specification using the proprietary method of specifying applicable to project specifications and master guide specifications. This Section specifies the “Fireframes® Curtainwall Series” a fire-rated steel frame system supplied by Technical Glass Products further described in Part 2 – Products.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

SECTION 08 44 18 - GLAZED STEEL CURTAIN WALL- FIREFRAMES® CURTAIN WALL SERIES

- GENERAL

      - Summary

        - Section Includes:

          - Fire-rated curtain wall systems, including perimeter trims, stools, accessories, shims and anchors, and perimeter sealing of curtain wall framing.

Verify that Section titles referenced below are correct for this Project's Specifications;. Revise the Section number and title below to suit project requirements, specification practices and section content. Refer to CSI MasterFormat for other section numbers and titles.

Verify other nearby items are specified. These include concrete and masonry inserts, concealed flashing

        - Related Sections include the following:

          - Section 05 12 00 “Structural Steel Framing:” Steel attachment members

          - Section 05 50 00  “Metal Fabrications:” Steel attachment members inserts and anchors

          - Section 07 25 00 “Weather Barriers:” Perimeter air, water and vapor seal between the work of this section and adjacent construction

          - Section 07 62 00 “Sheet Metal Flashing and Trim” Flashing between this work and other work

          - Section 07 84 00 – “Firestopping” for perimeter fire-containment systems (safing insulation) field installed with steel fire-rated glazed curtain-wall systems.

          - Section 07 92 00 – “Joint Sealants” for installation of joint sealants installed with steel fire-rated glazed curtain-wall systems and for sealants to the extent not specified in this Section.

          - Section 08 11 00 – “Metal Doors and Frames” for fire-rated doors.

          - Section 08 43 13 – “Aluminum Entrance and Storefronts” for entrance [and storefront] systems installed with steel fire-rated glazed curtain-wall systems.

          - Section 08 71 00 – “Door Hardware” for door hardware not provided by this Section.

          - Section 08 41 23 – “Fire Rated Steel Framed Entrances – Fireframes Heat Barrier Series” for fire-rated doors.

          - Section 08 41 23 – “Fire Rated Glass and Framing Systems – Fireframes Designer Series” for fire-rated doors.

      - REFERENCES

Adjust lists below to suit Project. Specifically this means to delete the types of finish that are not used AAMA 2603 through 2605 and if the system is used interiorly all the air and water infiltration testing and standards may be removed.

        - American Architectural Manufacturers Association (AAMA)

          - AAMA 501.1-2005: Standard Test Method for Water Penetration of Windows, Curtain Walls, and Doors Using Dynamic Pressure

          - AAMA 501.2-2003: Quality Assurance and Diagnostic Water Leakage Field Check of Installed Storefronts, Curtain Walls, and Sloped Glazing Systems

          - AAMA 501.4-2000 (Revised 2001): Recommended Static Test Method for Evaluating Curtain Wall and Storefront Systems Subjected to Seismic and Wind Induced Interstory Drifts

          - AAMA 501.5-2005: Test Method for Thermal Cycling of Exterior Walls

          - AAMA 506-2000 (Revised 2003): Voluntary Specifications for Hurricane Impact and Cycle Testing of Fenestration Products

          - AAMA 1503-1998: Voluntary Test Method for Thermal Transmittance and Condensation Resistance of Windows, Doors and Glazed Wall Sections

          - AAMA 2603-2002 - Voluntary Specification, Performance Requirements and Test Procedures for Pigmented Organic Coatings on Aluminum Extrusions and Panels.

          - AAMA 2604-2005 - Voluntary Specification, Performance Requirements and Test Procedures for High Performance Organic Coatings on Aluminum Extrusions and Panels.

          - AAMA 2605-2005 - Voluntary Specification, Performance Requirements and Test Procedures for Superior Performing Organic Coatings on Aluminum Extrusions and Panels.

        - American Society for Testing and Materials (ASTM):

          - Fire safety related:

            - ASTM E119:  Methods for Fire Tests of Building Construction and Materials.

          - Material related

            - ASTM A 1008/A 1008M - Standard Specification for Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength, Low Alloy, and High-Strength Low-Alloy with Improved Formability, Solution Hardened, and Bake Hardenable; 2007.

            - ASTM A 1011/A 1011M - Standard Specification for Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy and High-Strength Low-Alloy with Improved Formability, and Ultra-High Strength; 2006b.

          - Exterior related

            - ASTM E 283-04: Test Method for Determining the Rate of Air Leakage through Exterior Windows, Curtain Walls, and Doors under Specified Pressure Differences across the Specimen

            - ASTM E 330-02: Test Method for Structural Performance of Exterior Windows, Doors, Skylights and Curtain Walls by Uniform Static Air Pressure Difference Procedure A

            - ASTM E 331-04: Test Method for Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform Static Air Pressure Difference

            - ASTM E 783-02: Test Method for Field Measurement of Air Leakage through Installed Exterior Windows and Doors

            - ASTM E 1105-00: Test Method for Field Determination of Water Penetration of Installed Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform or Cyclic Static Air Pressure Difference

          - Hurricane related

            - ASTM E 1886-05: Test Method for Performance of Exterior Windows, Curtain Walls, Doors, and Impact Protective Systems Impacted by Missile(s) and Exposed to Cyclic Pressure Differentials

            - ASTM E 1996-05: Specification for Performance of Exterior Windows, Curtain Walls, Doors and Impact Protective Systems Impacted by Windborne Debris in Hurricanes

          - Sound related:

            - ASTM E 90-04: Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements

            - ASTM E 413-04: Standard Classification for Rating Sound Insulation

        - American Welding Society (AWS)

          - AWS D1.3 - Structural Welding Code - Sheet Steel; 2007

        - Builders Hardware Manufacturers Association, Inc

          - BHMA A156 - American National Standards for door hardware; 2006 (ANSI/BHMA A156).

        - Canadian Standards

          - CAN/ULC-S101 Standard Test of Fire Endurance Tests of Building Construction and Materials

          - CAN/ULC-S104 Standard Method of Fire Tests of Door Assemblies

          - CAN/ULC-S106 Standard Method of Fire Tests of Window and Glass Block Assemblies

        - National Fire Protection Association (NFPA):

          - NFPA 80:  Fire Doors and Windows.

          - NFPA 251:  Fire Tests of Building Construction & Materials

          - NFPA 252:  Fire Tests of Door Assemblies

          - NFPA 257:  Fire Test of Window Assemblies

        - Underwriters Laboratories, Inc. (UL):

          - UL 9:  Fire Tests of Window Assemblies

          - UL 10 B:  Fire Tests of Door Assemblies

          - UL 10 C:  Positive Pressure Fire Tests of Window & Door Assemblies

          - UL 263:  Fire tests of Building Construction and Materials

          - UL-752:  Ratings of Bullet-Resistant Materials

        - American National Standards Institute (ANSI):

          - ANSI Z97.1:  Standard for Safety Glazing Materials Used in Buildings

        - Consumer Product Safety Commission (CPSC):

          - CPSC 16 CFR 1201:  Safety Standard for Architectural Glazing Materials

        - American Society of Civil Engineers (ASCE)

          - ASCE 7 – Minimum Design Loads for Buildings and Other Structures; 2005

      - DEFINITIONS

        - Manufacturer:  A firm that produces primary glass, fabricated glass or framing as defined in referenced glazing publications.

      - Submittals

        - Submit in accordance with Section <Insert Section #>.

        - Product Data:

          - Technical Information:  Submit latest edition of manufacturer’s product data providing product descriptions, technical data, Underwriters Laboratories, Inc. listings and installation instructions.

        - Shop Drawings:

          - Include plans, elevations and details of product showing component dimensions; framed opening requirements, dimensions, tolerances, and attachment to structure

        - Sustainable Requirements:

          - Living Building Challenge Compliance:  Compliant

              - I-13 Red List Declaration

        - Structural Calculations (optional):

Structural Calculations recommended for exterior applications.

          - Provide structural calculations sealed by a licensed professional engineer in the State in which the project is located; prepared in compliance with referenced documents and these specifications.

        - Samples (optional).  For following products:

          - Glass sample-as provided by manufacturer

          - Sample of frame

          - Verification of sample of selected finish

        - Glazing Schedule: Use same designations indicated on drawings for glazed openings in preparing a schedule listing glass types and thicknesses for each size opening and location.

        - Warranties:  Submit manufacturer’s warranty.

        - Certificates of compliance from glass and glazing materials manufacturers attesting that glass and glazing materials furnished for project comply with requirements.

          - Separate certification will not be required for glazing materials bearing manufacturer’s permanent label designating type and thickness of glass, provided labels represent a quality control program involving a recognized certification agency or independent testing laboratory acceptable to authority having jurisdiction.

      - QUALITY ASSURANCE

        - Testing Agency Qualifications:  Qualifications according to

          - International Accreditation Service for a Type A Third-Party Inspection Body (Field Services ICC-ES Third-Party Inspections Standard Operating Procedures, 00-BL-S0400 and S0401)

          - International Accreditation Service for Testing Body-Building Materials and Systems

            - Fire Testing

              - ASTM Standard E119

              - CPSC Standard 16 CFR 1201

              - NFPA Standards 251, 252, 257

              - UL Standards 9, 10B, 10C, 1784, UL Subject 63

              - BS 476; Part 22:  1987

              - EN 1634-1

              - CAN/ULC Standards S101, S104, S106

        - Environmental Qualifications

          - Living Building Challenge Compliant and Red List Approved

            - Declare label (#AGN-0010)

            - https://declare.living-future.org/products/technical-glass-products-fireframes-curtainwall-series and can be used for building projects seeking to achieve either the Living Building Challenge or LEED green building rating systems.

        - Installer Qualifications:  An experienced installer who has completed glazing similar in material, design, and extent to that indicated for this Project; whose work has resulted in glass installations with a record of successful in-service performance; and who employs glass installers for this Project who are certified under the National Glass Association Glazier Certification Program as Level 2 (Senior Glaziers) or Level 3 (Master Glaziers).

Delete paragraph above or below.  If retaining above, verify with prospective installers that they can comply with glazier qualifications.

        - Installer Qualifications: An experienced installer who has completed glazing similar in material, design, and extent to that indicated for Project and whose work has resulted in construction with a record of successful in-service performance.

        - Source Limitations for Glazing Accessories:  Obtain glazing accessories from one source for each product and installation method indicated.

        - Fire-Rated Window Assemblies:  Assemblies complying with NFPA 80 that are classified and labeled by UL, for fire ratings indicated, based on testing according to NFPA 257 and UL 9.   For 45-minute fire-rated assemblies only.

        - Fire-Rated Wall Assemblies: Assemblies complying with ASTM E119 that are classified and labeled by UL, for fire ratings indicated, based on testing in accordance with UL 263, ASTM E119.

Generally retain first paragraph below unless types of glass do not require labeling by authorities having jurisdiction or if certification is required as well as labels.

        - Listing and Labels – Fire-Rated Assemblies:  Under current follow-up service by Underwriters Laboratories® maintaining a current listing or certification. Label assemblies accordance with limits of manufacturer’s listing.

      - Delivery, Storage, and Handling

        - Deliver, store and handle under provisions specified by manufacturer.

      - PROJECT CONDITIONS

        - Obtain field measurements prior to fabrication of frame units.  If field measurements will not be available in a timely manner, coordinate planned measurements with the work of other sections.

          - Note whether field or planned dimensions were used in the creation of the shop drawings

        - Coordinate the work of this sections with others effected including but not limited to:  other interior and /or exterior envelope components and door hardware beyond that provided by this section.

      - WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

        - Provide the Pilkington Pyrostop® and the Fireframes® Curtainwall Series standard five-year manufacturer warranty.

- PRODUCTS

      - Manufacturers (Acceptable Manufacturers/Products)

        - Manufacturer Glazing Material:  “Pilkington Pyrostop®” fire-rated glazing as manufactured by the Pilkington Group and distributed by Technical Glass Products, 8107 Bracken Place SE, Snoqualmie, WA  98065 phone (800.426.0279)  e-mail tgp.sales@allegion.com, web site http://www.fireglass.com.

        - Frame System:  Fireframes® Curtainwall Series fire-rated steel frame system as supplied by Technical Glass Products 8107 Bracken Place SE, Snoqualmie, WA  98065 phone (800.426.0279) e-mail tgp.sales@allegion.com, web site http://www.fireglass.com.

        - Substitutions:  Substitutions for Glazing Material and Frame System not permitted.

      - PERFORMANCE REQUIREMENTS

Select the widths used for facility under design

        - System Description:

          - Steel fire-rated glazed curtain wall system, outside glazed pressure plate, cover cap format.

          - Face Widths Available:

            - 1 3/4-inch.

            - 2 3/8-inch wide.

          - Water Drainage:

          - System is vertically weeped. No joint plugs or weep holes at horizontal mullions. Horizontal gaskets are notched and received by vertical gaskets.

        - Structural Performance

          - Design and size the system to withstand structural forces placed upon it without damage or permanent set when tested in accordance with ASTM E330 using load 1.5 times the design wind loads and of 10 seconds in duration.

          - Positive wind load: [______lbf/sq ft.][as indicated on the drawings]

          - Negative wind Load:[______lbf/sq ft.][as indicated on the drawings]

          - Member deflection: Limit deflection of the edge of the glass normal to the plane of the glass to [flexure limit of glass][1/175 of the glass edge length or ¾ inch, whichever is less][of any framing member

          - Accommodate movement between storefront and adjoining systems

        - Air Infiltration:  ASTM E 283; Air infiltration rate shall not exceed 0.06 cfm/ft2 at a static air pressure differential of 6.24 psf.

        - Water Resistance, (static):  ASTM E 331; No leakage at a static air pressure differential of 15 psf as defined in AAMA 501.

        - Water Resistance, (dynamic):  AAMA 501.1; No leakage at an air pressure differential of 15 psf as defined in AAMA 501.

        - Thermal Movements:  Provide steel fire-rated glazed curtain-wall systems that allow for thermal movements resulting from the following maximum change (range) in ambient and surface temperatures.  Base engineering calculation on surface temperatures of materials due to both solar heat gain and nighttime-sky heat loss.

Differential values below (for aluminum in particular) are suitable for most of the U.S.  Revise to suit local conditions and metal color and finish.

          - Temperature Change (Range):  120 deg F (67 deg C), ambient; 180 deg F (100 deg C), material surfaces.

      - MATERIALS - GLASS

        - Low-E Coated glass for use in insulated exterior units See Section 08 80 00. See chart below for Low-E configurations.

        - Use the paragraph above to specify the low-e coated glass in Section 08 80 00 and use the paragraph below to select glass available from Technical Glass Products. Other manufacturer’s glass will need to be shipped to Technical Glass Products for incorporation into insulated unit.

        - Not all Low-E coated glass by all manufacturers is available for assembly by others into insulated units. Consult with low-e glass manufacturer about availability of their low-e product for shipment to Technical Glass Products for inclusion into insulated units.

        - Fire Rated Glazing:  Composed of multiple sheets of Pilkington “Optiwhite™” high visible light transmission glass laminated with an intumescent interlayer.

        - Impact Safety Resistance:  ANSI Z97.1 and CPSC 16CFR1201 (Cat. I and II).

        - Adjust list of thicknesses below to suit Project -- these are listed in tabular form delete those columns not used.

        - Properties Interior Glazing

| Property |  |  |  |  |
| --- | --- | --- | --- | --- |
| Fire Rating | 45 minute | 60 minute |  | 120 minute |
| Manufacturer’s designation | 45-200 | 60-101 | 60-201 | 120-104 |
| Glazing type | single | single | single | IGU |
| Nominal Thickness | 3/4” (19mm) | 7/8” (23mm) | 1-1/16” (27mm) | 2-1/8 (54mm) [with 8 mm spacer, or 2-3/8” (60 mm) with 14 mm spacer] |
| Weight in lbs/sf | 9.2 | 10.85 | 12.5 | 21.7 |
| Daylight Transmission | 86% | 87% | 86% | 75% |
| Sound Transmission Coefficient | 40dB | 41dB | 44dB | 46dB |

        - Properties Exterior Glazing

| Property | 45 minute |  | 60 minute |  | 120 minute |
| --- | --- | --- | --- | --- | --- |
| Manufacturer’s designation | 45-200 | 45-260 45-360 | 60-201 | 60-261 60-361* | 120-262 120-362* |
| Glazing type | single | IGU | single | IGU | IGU |
| Nominal Thickness | 3/4” (19mm) | 1-5/16” (33mm) | 1-1/16” (27mm) | 1-5/8” (41mm) | 2-3/8" (60mm) [with 14 mm spacer, or 2-1/8” (54 mm) with 8 mm spacer] |
| Weight in lbs/sf | 9.2 | 12.5 | 12.5 | 15.8 | 22.1 |
| Daylight Transmission | 86 | 77 | 86% | 77% | 74% |
|  |  | 59-71 |  | 59-70% | 33-68% |
| Sound Transmission Coefficient | 40dB | 40dB | 44dB | 44dB | 46dB |

- * Low-E product.

        - Exterior Grade:  PVB inner layer installed toward exterior.

        - Logo:  Each piece of fire-rated glazing shall be labeled with a permanent logo including name of product, manufacturer, testing laboratory (UL), fire rating period, safety glazing standards, and date of manufacture.

        - Glazing Accessories:  Manufacturer’s standard compression gaskets, spacers, setting blocks and other accessories necessary for a complete installation.

      - MATERIALS –STEEL FRAMING

        - Steel Curtainwall Framing System [45 min.] [60 min.] [120 min]

          - Frame: [Steel]:  profiled steel tubing permanently joined with steel bolts.

          - Insulation:  Insulate framing system against effects of fire, smoke, and heat transfer from either side. Firmly pack perimeter of framing system to rough opening with mineral wool fire stop insulation or appropriately rated intumescent sealant

          - Fasteners:  Type recommended by manufacturer

          - Glazing Gaskets, Compounds and tapes:  Glaze Pilkington Pyrostop glass with approved EPDM glazing gaskets and [closed cell PVC tape], or [pure silicone sealant].

          - Steel Pressure Plates:  Formed stainless steel pressure plate with dimensions recommended by manufacturer to securely hold glazing material in place.

          - Cover Caps:  Formed [steel] [stainless steel] [extruded aluminum].

        - Aluminum:  Alloy and temper recommended by manufacturer for type of use and finish indicated.

          - Extruded Bars, Rods, Shapes, and Tubes:  ASTM B 221 (ASTM B 221M).

        - Steel Reinforcement:  With manufacturer's standard corrosion-resistant primer complying with SSPC-PS Guide No. 12.00 applied immediately after surface preparation and pretreatment.  Select surface preparation methods according to recommendations in SSPC-SP COM and prepare surfaces according to applicable SSPC standard.

          - Structural Shapes, Plates, and Bars:  ASTM A 36/A 36M Standard Specification for Carbon Structural Steel

          - Cold-Rolled Sheet and Strip:   ASTM A1008/A1008M  Standard Specification for Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, Required Hardness, Solution Hardened, and Bake Hardenable

          - Hot-Rolled Sheet and Strip:   ASTM A1011/A1011M Standard Specification for Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, and Ultra-High Strength

        - Brackets and Reinforcements:  Manufacturer's standard high-strength materials with nonstaining, nonferrous shims for aligning system components.

        - Fasteners and Accessories:  Manufacturer's standard corrosion-resistant, nonstaining, nonbleeding fasteners and accessories compatible with adjacent materials.

          - Where fasteners are subject to loosening or turn out from thermal and structural movements, wind loads, or vibration, use self-locking devices.

          - Reinforce members as required to receive fastener threads.

        - Anchors:  Three-way adjustable anchors that accommodate fabrication and installation tolerances in material and finish compatible with adjoining materials and recommended by manufacturer.

Delete subparagraph below if not applicable or revise to suit Project.

          - Concrete and Masonry Inserts:  Hot-dip galvanized cast-iron, malleable-iron, or steel inserts complying with ASTM A 123/A 123M or ASTM A 153/A 153M requirements.

        - Concealed Flashing:  Manufacturer's standard corrosion-resistant, nonstaining, nonbleeding flashing compatible with adjacent materials.

      - Accessories

        - Exposed Fasteners:  Use fasteners fabricated from Type 304 or Type 316 stainless steel.

        - Glazing Gaskets:

          - Glazing gaskets for interior or exterior applications:  ASTM C 864 (extruded EPDM rubber that provides for silicone adhesion) or ASTM C1115 Standard Specification for Dense Elastomeric Silicone Rubber Gaskets and Accessories (extruded silicone).

        - Intumescent Tape:  As supplied by frame manufacturer.

        - Setting Blocks:  ¼” Calcium silicate.

        - Perimeter Anchors:  Steel or 316 Stainless steel when exposed.

        - Flashings:  As recommended by manufacturer; same material and finish as cover caps.

        - Silicone Sealant:  One-Part Low Modulus, neutral cure High Movement-Capable Sealant: Type S; Grade NS; Class 25 with additional movement capability of 100 percent in extension and 50 percent in compression (total 150 percent); Use (Exposure) NT; Uses (Substrates) M, G, A, and O as applicable. (Use-O joint substrates include: Metal factory-coated with a high-performance coating; galvanized steel; ceramic tile.)

          - Available Products:

            - Dow Corning 790, 795 - Dow Corning Corp.

            - Momentive

            - Tremco

        - Intumescent Caulk:  Single component, latex-based, intumescent caulk designed to stop passage of fire, smoke, and fumes through fire-rated separations; permanently flexible after cure; will not support mold growth; flame spread/smoke developed 10/10.

          - Available Products:

            - 3M CP 25WB+.

      - SLAG-WOOL-FIBER/ROCK-WOOL-FIBER INSULATION

        - Available Manufacturers:

          - Fibrex Insulations Inc.

          - Owens Corning

          - Thermafiber

          - Rockwool

        - Unfaced, Slag-Wool-Fiber/Rock-Wool-Fiber Board Insulation:  ASTM C 612, maximum flame-spread and smoke-developed indexes of 15 and 0, respectively; passing ASTM E 136 for combustion characteristics; and of the following nominal density and thermal resistivity:

          - Nominal density of 4 lb/cu. ft. (64 kg/cu. m), Types IA and IB, thermal resistivity of 4 deg F x h x sq. ft./Btu x in. at 75 deg F (27.7 K x m/W at 24 deg C).

          - Fiber Color:  Regular color, unless otherwise indicated.

      - Fabrication

        - General:

          - Fabricate components per manufacturer's installation instructions and with minimum clearances and shim spacing around perimeter of assembly yet enabling installation and dynamic movement of perimeter seal.

          - Accurately fit and secure joints and corners. Make joints flush and weatherproof.

          - Prepare components to receive anchor devices.

          - Provide physical and thermal isolation of glazing from framing members.

          - Provide internal guttering to drain water from joints and condensation occurring within glazing pocket.

          - Fabricate anchors.

          - Arrange fasteners and attachments to be concealed from view.

        - Guttered System Components:

          - Fabricate components to resist water penetration as follows:

            - Internal guttering system or other means to drain water passing joints, occurring within framing members, and moisture migrating within glazed steel curtain walls.

            - Pressure-equalized system, double barrier, or two lines of air and water resistance design with primary air and water barrier at interior side of glazing pocket.

      - POWDER COAT FINISHES

        - Finish after fabrication.

        - Appearance of Finished Work: Variations in appearance of abutting or adjacent pieces are acceptable. Noticeable variations in the same piece are not acceptable.

        - Interior and Exterior Steel Finishes (Note: this finish is suitable for exterior exposed portions of the wall systems, including extruded aluminum covers).

          - Powder-Coat Finish: Polyester Super Durable powder coating which meets AAMA 2604 for chalking and fading. Apply manufacturer's standard powder coating finish system applied to factory-assembled frames before shipping, complying with manufacturer's recommended instructions for surface preparation including pretreatment, application, and minimum dry film thickness.

          - Color and Gloss: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

          - Acceptable Manufacturers:

            - Tiger Drylac

            - Additional manufacturers as approved by TGP

      - ALUMINUM FINISHES

        - Finish designations prefixed by AA comply with the system established by the Aluminum Association for designating aluminum finishes.

Retain finishes below to suit Project.  If retaining more than one, indicate location of each on Drawings or by inserts.  Revise mechanical finish if custom finish is required and availability is verified.

        - Class II, Clear Anodic Finish:  AA-M12C22A31 (Mechanical Finish:  nonspecular as fabricated; Chemical Finish:  etched, medium matte; Anodic Coating:  Architectural Class II, clear coating 0.010 mm or thicker) complying with AAMA 611.

Above is standard finish with many manufacturers; below is heavy-anodized finish.  Verify availability with manufacturers selected.

        - Class I, Clear Anodic Finish:  AA-M12C22A41 (Mechanical Finish:  nonspecular as fabricated; Chemical Finish:  etched, medium matte; Anodic Coating:  Architectural Class I, clear coating 0.018 mm or thicker) complying with AAMA 611.

        - Class II, Color Anodic Finish:  AA-M12C22A32/A34 (Mechanical Finish:  nonspecular as fabricated; Chemical Finish:  etched, medium matte; Anodic Coating:  Architectural Class II, integrally colored or electrolytically deposited color coating 0.010 mm or thicker) complying with AAMA 611.

Delete paragraph above or below.  Verify availability with manufacturers selected.

        - Class I, Color Anodic Finish:  AA-M12C22A42/A44 (Mechanical Finish:  nonspecular as fabricated; Chemical Finish:  etched, medium matte; Anodic Coating:  Architectural Class I, integrally colored or electrolytically deposited color coating 0.018 mm or thicker) complying with AAMA 611.

Retain one color below with either class of color anodic finish above.

          - Color:  [Light bronze] [Medium bronze] [Dark bronze] [Black].

Options in subparagraph above are examples only and may vary in color range and availability among manufacturers.  Retain one or delete all and retain one of two options in subparagraph below.

          - Color:  [Match Architect's sample] [As selected by Architect from full range of industry colors and color densities].

Paragraph below references AAMA standards for high-performance and superior performance organic coatings on extrusions and panels.  Revise if specific products are required.

        - High-Performance Organic Finish (2-Coat Fluoropolymer):  AA-C12C40R1x (Chemical Finish:  cleaned with inhibited chemicals; Chemical Finish:  conversion coating; Organic Coating:  manufacturer's standard 2-coat, thermocured system consisting of specially formulated inhibitive primer and fluoropolymer color topcoat containing not less than 70 percent polyvinylidene fluoride resin by weight).  Prepare, pretreat, and apply coating to exposed metal surfaces to comply with AAMA [2604] [2605] and with coating and resin manufacturers' written instructions.

Delete paragraph above or below; if both are required, indicate location of each system on Drawings, in schedules, or by inserts.

Paragraph below references AAMA standard for superior performance organic coating on extrusions and panels.  Revise if specific products are required.

        - High-Performance Organic Finish (3-Coat Fluoropolymer):  AA-C12C40R1x (Chemical Finish:  cleaned with inhibited chemicals; Chemical Finish:  conversion coating; Organic Coating:  manufacturer's standard 3-coat, thermocured system consisting of specially formulated inhibitive primer, fluoropolymer color coat, and clear fluoropolymer topcoat, with both color coat and clear topcoat containing not less than 70 percent polyvinylidene fluoride resin by weight).  Prepare, pretreat, and apply coating to exposed metal surfaces to comply with AAMA 2605 and with coating and resin manufacturers' written instructions.

Retain one color and gloss below with either paragraph above.

          - Color and Gloss:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

- EXECUTION

      - Examination

        - Site Verification of Conditions: Verify substrate conditions (which have been previously installed under other sections) are acceptable for product installation in accordance with manufacturer’s instructions. Verify openings are sized to receive curtain wall system and sill plate is level in accordance with manufacturer’s acceptable tolerances.

        - Notify Architect of any conditions which jeopardize the integrity of the proposed fire wall / door system.

        - Do not proceed until such conditions are corrected.

      - Installation

        - See Fireframes Curtainwall Series Installation Manual

      - Protection and Cleaning

        - Protect glass from damage immediately after installation by attaching crossed streamers to framing held away from the glass.  Do not apply markers to the glass surface.  Remove nonpermanent labels, and clean surfaces.

          - Do not clean with astringent cleaners. Use a clean “grit free” cloth and a small amount of mild soap and water or mild detergent.

          - Do not use any of the following:

            - Steam jets

            - Abrasives

            - Strong acidic or alkaline detergents, or surface-reactive agents

            - Detergents not recommended in writing by the manufacturer

            - Do not use any detergent above 77 degrees F

            - Organic solvents including but not limited to those containing ester, ketones, alcohols, aromatic compounds, glycol ether, or halogenated hydrocarbons.

            - Metal or hard parts of cleaning equipment must not touch the glass surface

        - Protect glass from contact with contaminating substances resulting from construction operations, including weld splatter.  If, despite such protection, contaminating substances do come into contact with glass, remove them immediately as recommended by glass manufacturer.

Modify paragraph below to suit Project.

        - Wash glass on both exposed surfaces in each area of Project not more than four days before date scheduled for inspections that establish date of Substantial Completion.  Wash glass as recommended by glass manufacturer.

END OF SECTION 08900