Technical Glass Products has included notes in this specification to assist you in tailoring the content to your project.  These comments will appear on your screen in blue.  To hide them and view only the specification, do the following:

Click the “Office” button and then click the word “Options” OR select the “File” and then click “Options”.   Click “Display” at the left of the dialog box.  Remove the check mark from the “Hidden Text” box.  Then click “OK.”  All blue text will then be hidden.

This document is designed for use by a qualified construction specifier. Proper modifications are required to tailor this specification to your project needs.  Optional text is placed between brackets “[ ].”  Blank underlines  “__” represent areas you need to fill in with your project specific information. For assistance, call Technical Glass Products at 1-800-426-0279.

This guide specification is a supplier-specific proprietary product specification using the proprietary method of specifying applicable to project specifications and master guide specifications. This Section specifies the “Fireframes Designer Series” a fire-rated steel frame system supplied by Technical Glass Products further described in Part 2 – Products.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

SECTION 08 41 23 – STEEL FRAMED ENTRANCES AND STOREFRONTS - SMOKESAFE™ WINDOW & DOOR SYSTEM

GENERAL

SUMMARY

Section Includes:

Smoke-rated door and window framing system for installation as (choose one or more as applicable) [full vision doors] [sidelights] [borrowed lights] [windows] [transoms] in interior openings.

Verify that Section titles referenced below are correct for this Project's Specifications; Revise the Section number and title below to suit project requirements, specification practices and section content. Refer to CSI MasterFormat for other section numbers and titles.

Verify other nearby items are specified. These include concrete and masonry inserts, concealed flashing.

Related Sections:

Section 05 12 00 “Structural Steel Framing:” Steel attachment members

Section 05 50 00  “Metal Fabrications:” Steel attachment members inserts and anchors

Section 07 62 00 “Sheet Metal Flashing and Trim” Flashing between this work and other work

Section 08 11 13 “Hollow Metal Doors and Frames.” Hollow Metal doors prepped for the work of this section.

Section 08 71 00 “Door Hardware:” Door hardware other than that provided by the work of this section

Section 08 71 13 “Automatic Door Operators” opener for door to comply with ADA and Local Authority opening force requirements.

REFERENCES

Adjust lists below to suit Project.. Specifically this means to delete the types of finish that are not used AAMA 2603 thru 2605 and if the system is used in interior applications all the air and water infiltration testing and standards may be removed.

American Architectural Manufacturers Association (AAMA)

AAMA 2603-2002 - Voluntary Specification, Performance Requirements and Test Procedures for Pigmented Organic Coatings on Aluminum Extrusions and Panels.

AAMA 2604-2005 - Voluntary Specification, Performance Requirements and Test Procedures for High Performance Organic Coatings on Aluminum Extrusions and Panels.

AAMA 2605-2005 - Voluntary Specification, Performance Requirements and Test Procedures for Superior Performing Organic Coatings on Aluminum Extrusions and Panels.

American Society for Testing and Materials (ASTM):

Material related

ASTM A 1008/A 1008M - Standard Specification for Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength, Low Alloy, and High-Strength Low-Alloy with Improved Formability, Solution Hardened, and Bake Hardenable; 2007.

ASTM A 1011/A 1011M - Standard Specification for Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy and High-Strength Low-Alloy with Improved Formability, and Ultra-High Strength; 2006b.

Sound related:

ASTM E 90-04: Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements

ASTM E 413-04: Standard Classification for Rating Sound Insulation

American Welding Society (AWS)

AWS D1.3 - Structural Welding Code - Sheet Steel; 2007

Builders Hardware Manufacturers Association, Inc.

BHMA A156 - American National Standards for door hardware; 2006 (ANSI/BHMA A156).

National Fire Protection Association (NFPA):

NFPA 80:  Standard for Fire Doors and Fire Windows.

NFPA 105: Standard for the Installation of Smoke Door Assemblies

NFPA 251:  Standard Methods of Tests of Fire Endurance of Building Construction and Materials.

NFPA 252:  Standard Methods of Fire Tests of Door Assemblies.

NFPA 257:  Standard on Fire Test for Window and Glass Block Assemblies.

Underwriters Laboratories, Inc. (UL):

UL 9:  Fire Tests of Window Assemblies.

UL 10B:  Fire Tests of Door Assemblies.

UL 10C:  Positive Pressure Fire Tests of Door Assemblies.

UL 1784: Air Leakage Tests for Door Assemblies.

American National Standards Institute (ANSI):

ANSI Z97.1:  Standard for Safety Glazing Materials Used in Buildings.

Consumer Product Safety Commission (CPSC):

CPSC 16 CFR 1201 Categories I and II:  Safety Standard for Architectural Glazing Materials.

American Society of Civil Engineers (ASCE)

ASCE 7 – Minimum Design Loads for Buildings and Other Structures; 2005

DEFINITIONS

Manufacturer:  A firm that produces primary glass, fabricated glass or framing as defined in referenced glazing publications.

SUBMITTALS

Submit in accordance with Section <Insert Section #>.

Product Data:

Technical Information:  Submit latest edition of manufacturer’s product data providing product descriptions, technical data, Underwriters Laboratories, Inc. listings and installation instructions.

Shop Drawings:

Include plans, elevations and details of product showing component dimensions; framed opening requirements, dimensions, tolerances, and attachment to structure

Hardware schedule: list of manufacture supplied hardware and verification of cylinder size complying with Section 08 71 00

Samples (optional):   For following products:

Glass sample-as provided by manufacturer

Sample of frame

Verification of sample of selected finish

Glazing Schedule:  Use same designations indicated on drawings for glazed openings in preparing a schedule listing glass types and thicknesses for each size opening and location.

Warranties: Submit manufacturer’s warranty.

Certificates of compliance from glass and glazing materials manufacturers attesting that glass and glazing materials furnished for project comply with requirements.

Separate certification will not be required for glazing materials bearing manufacturer’s permanent label designating type and thickness of glass, provided labels represent a quality control program involving a recognized certification agency or independent testing laboratory acceptable to authority having jurisdiction.

QUALITY ASSURANCE

Testing Agency Qualifications: Qualified according to

International Accreditation Service for a Type A Third-Party Inspection Body (Field Services ICC-ES Third-Party Inspections Standard Operating Procedures, 00-BL-S0400 and S0401)

International Accreditation Service for Testing Body-Building Materials and Systems

Smoke Testing

NFPA Standards 105

UL Standards 1784

Installer Qualifications:  An experienced installer who has completed glazing similar in material, design, and extent to that indicated for this Project; whose work has resulted in glass installations with a record of successful in-service performance; and who employs glass installers for this Project who are certified under the National Glass Association Glazier Certification Program as Level 2 (Senior Glaziers) or Level 3 (Master Glaziers).

Delete paragraph above or below.  If retaining above, verify with prospective installers that they can comply with glazier certification requirements.

Installer Qualifications:  An experienced installer who has completed glazing similar in material, design, and extent to that indicated for Project and whose work has resulted in construction with a record of successful in-service performance.

Source Limitations for Glazing Accessories:  Obtain framing system, glazing and glazing accessories from one source for each product and installation method indicated.

Generally retain paragraph below unless types of glass selected do not require labeling by authorities having jurisdiction or if certification is required as well as labels.

Listings and Labels – Smoke-Rated Assemblies:  Under current follow-up service by Underwriters Laboratories® maintaining a current listing or certification. Label assembly accordance with limits of manufacturer’s listing for smoke resistance.

Regulatory Requirements:  Comply with provisions of the following:

Generally retain Americans with Disabilities Act Accessibility Guidelines below for private projects; FED-STD-795 for Federal, State, and local government projects.  Verify with authorities having jurisdiction.

Where indicated to comply with accessibility requirements, comply with [Americans with Disabilities Act (ADA), "Accessibility Guidelines for Buildings and Facilities (ADAAG),"] [ANSI A117.1,] [FED-STD-795, "Uniform Federal Accessibility Standards,"] as follows:

Handles, Pulls, Latches, Locks, and other Operating Devices:  Shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist.

Door Closers:  Comply with the following maximum opening-force requirements indicated:

Accessible doors no more than 5 lbf (22.2 N) push or pull force

Smoke-Rated Doors:  Minimum opening force allowable by authorities having jurisdiction

DELIVERY, STORAGE AND HANDLING

Deliver, store and handle under provisions specified by manufacturer.

      - PROJECT CONDITIONS

Obtain field measurements prior to fabrication of frame units. If field measurements will not be available in a timely manner coordinate planned measurements with the work of other sections.

Note whether field or planned dimensions were used in the creation of the shop drawings.

### Coordinate the work of this section with others effected including but not limited to: other interior and/or exterior envelope components and door hardware beyond that provided by this section

      - WARRANTY

Provide the SmokeSafe™ Window and Door System standard five-year manufacturer warranty.

PRODUCTS

Adjust options in Article below to suit Project.

Manufacturers – SMOKE-RATED [DOOR ASSEMBLY] [WINDOW] SYSTEM

Frame System:  “SmokeSafe™ Window & Door System by TGP” smoke-rated [steel] [brushed stainless steel] frame system as manufactured and supplied by Technical Glass Products, 8107 Bracken Place SE, Snoqualmie, WA  98065 phone (800.426.0279) fax (425.396.8300) e-mail tgp.sales@allegion.com web site http://www.fireglass.com.

Adjust list of products in paragraph below to suit Project.

Glass Material:  [Tempered Monolithic][Tempered Insulated Glass Unit][Laminated][Laminated Insulated Glass Unit] as fabricated and distributed by Technical Glass Products, 8107 Bracken Place SE, Snoqualmie, WA  98065 phone (800.426.0279) fax (425.396.8300) e-mail tgp.sales@allegion.com, web site http://www.fireglass.com.

Substitutions:  Substitutions for Glazing Material and Frame System not permitted.

performance requirements

Adjust minutes in paragraphs below to suit Project. (choose one or more as applicable)

Smoke Rating Requirements

General:  Provide ICU/CCU entrances capable of withstanding structural loads and thermal movements based on testing manufacturer's standard units in assemblies similar to those indicated for this Project.

Smoke and Draft Control: Provide smoke and draft control system on specified doors.  Smoke and draft control system shall provide an effective barrier for limiting the passage of smoke through door assemblies. Smoke and draft control system shall comply with the following:

The maximum air leakage rate for door assemblies shall be 3.0 ft3/min/ft2 (0.9 m3/min/m2) of door opening at 0.30 in water column (75 Pa) for both the ambient and elevated temperature tests.

Door shall be tested in accordance UL 1784.

Installation shall be in accordance with NFPA 105.

Design Requirements:

Dimensions – Door and Framing:

Door framing face dimension:  1-15/16-inch.

Depth of door framing:  1-15/16-inch.

Door style face dimension:  3-1/8-inch.

Door cross rail (if applicable) face:  3-9/16-inch.

Depth of stile, header, sill and cross rail:  1-15/16-inch

Dimensions -- Window Assembly:

Perimeter framing face dimension:  2-3/4-inch at head, sill and jamb.

Horizontal and/or vertical mullions:  3-9/16-inch on the face.

Depth of perimeter and mullion:  1-15/16-inch.

Construction:  Narrow-profile, roll-formed steel architectural grade specialty fire doors.  Conventional break-shape type hollow metal steel fire-rated doors will not be considered an acceptable substitute for the SmokeSafe™ Window & Door System specified in this section as they do not conform to the project design intent and/or aesthetic and quality standards.

Knock down frames are permitted.

ASTM E330 procedure A is a test method that describes the determination of the structural performance of exterior windows, doors, skylights, and curtain walls under uniform static air pressure differences, using a test chamber. The test is intended only for evaluating the structural performance associated with the specified test specimen and not the structural performance of adjacent construction.

Member deflection is referenced from the IBC Section 24 General Requirements for Glass, article 2403.3.

MATERIALS - GLASS

Glazing:  ASTM C 1036 and ASTM C 1048; [Tempered Monolithic] [Tempered Insulated Glass Unit][Laminated][Laminated Insulated Glass Unit]

Adjust list of products and thicknesses below to suit Project.

Thickness of Glazing Material:

Tempered Monolithic:  1/4” (6 mm) glass

Tempered IGU: 1" (25 mm) IGU: 1/4” (6 mm) tempered glass + 1/2” (12 mm) air space + 1/4” (6 mm) tempered glass

Laminated: 1/8” (3 mm) glass + .03” (.76 mm) PVB 1/8” (3 mm) glass

Laminated IGU: 1" (25 mm) IGU: 1/8” (3 mm) glass + .03” (.76 mm) PVB + 1/8” (3 mm) glass

+ 1/2” (12 mm) air space +1/4” (6 mm) tempered glass

Approximate Visible Transmission:  Varies with thickness (approximate range 85-90 percent).

Labeling:

Frame logo:  Assembly must bear permanent label indicating it as a smoke-rated door/system.

Glass Logo:  Labeling should comply with the ANSI Z97.1 and/or CPSC safety standards.

Performance:  Glass must be safety rated to meet requirements of CPSC 16 CFR 1201 Categories I and II.

MATERIALS – STEEL FRAMES AND DOORS

Adjust paragraphs below to suit Project.

Steel Framing System including doors, sidelites, transoms and windows.

Frame:  [Steel] [brushed stainless steel] profiled formed tubing.

Fasteners:  As recommended by manufacturer

Glazing Accessories:  calcium silicate setting blocks.

Adjust paragraphs below to suit Project, Glazing tape comes in 45 and 90 minute tested varieties.

Fabrication

Furnish frame assemblies pre-welded.

When necessary, splice frames too large for shop fabrication or shipping or to fit in available building openings.

Fit with suitable fasteners.

Knock-down (“K-D”) frames are permitted

Furnish interior frame assemblies “K-D” (or welded upon request).

When necessary, splice frames too large for shop fabrication or shipping or to fit in available building openings.

Fit with suitable fasteners.

Knock-down door perimeter frames are not permitted

Field glaze door and frame assemblies.

Factory prepare steel door assemblies and install all hardware.

Fabrication Dimensions:  Fabricate to smoke-rated field dimensions.

Obtain approved shop drawings prior to fabrication.

FINISHES, GENERAL

Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

Finish frames after assembly.

Appearance of Finished Work:  Variations in appearance of abutting or adjacent pieces are acceptable.  Noticeable variations in the same piece are not acceptable.

Powder coat finish systems offered and provided by Technical Glass Products are manufactured by Tiger Drylac which is a hybrid powder coating for interior applications based on a blend of epoxy-polyester. If used exteriorly contact your Technical Glass Product Representative for alternative finishes that provide an even higher standard of protection.

POWDERCOAT FINISHES

Finish after fabrication.

Appearance of Finished Work:	Variations in appearance of abutting or adjacent pieces are acceptable. Noticeable variations in the same piece are not acceptable.

Interior and Exterior Steel Finishes (Note: this finish is suitable for exterior exposed portions of the wall systems, including extruded aluminum covers).

Powder-Coat Finish: Polyester Super Durable powder coating which meets AAMA 2604 for chalking and fading. Apply manufacturer's standard powder coating finish system applied to factory-assembled frames before shipping, complying with manufacturer's recommended instructions for surface preparation including pretreatment, application, and minimum dry film thickness.

Color and Gloss: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

Acceptable Manufacturers:

Tiger Drylac

Additional manufacturers as approved by TGP

DOOR HARDWARE

Furnish hardware with air leakage-rated door by the manufacturer.

Select hardware from door manufacturer's standard recommended and approved hardware groups as specified in Division 8 Section – Door Hardware.

Provide power assisted hardware for use at any door that cannot meet the opening force(s) required by code noted in Part I above.

High energy, power-operated doors must meet the requirements of ANSI/BHMA A156.10 and power-assisted low energy doors must comply with ANSI/BHMA A156.19

SmokeSafe™ Window and Door System features narrow steel profiles which exceed traditional smoke-rated frame systems in aesthetics and performance.

TGP offers a complete line of select hardware options which have been fit and function-tested for use with these profiles. Not all hardware components available are compatible with SmokeSafe Window and Door System’s narrow profile systems. Some hardware items may require a wide stile profile, and some hardware items may not be used at all to be compliant with the smoke-rated system. Should you request an item of hardware not standardly supplied by TGP, please forward all relevant information (manufacturer, model number, fabrication template and if required physical sample) to TGP for evaluation to determine if it can be supplied by TGP for use. Use of non-standard hardware may incur additional cost and lead time.

Compare door swing types (LH, RH, LHR, etc.) from the Door Handing Chart in the TGP SmokeSafe™ Window & Door Architectural Specification Manual to the chart’s types to see available hardware standards and options for each door swing combination. For detailed hardware information refer to the individual cut sheets available from Technical Glass Products.

Finish Legend:

- PTM	Powder coated to match frame

- MA	Mill Finish Aluminum

- 689	Aluminum Paint

- 630	Satin Stainless Steel

- 626	Satin Chrome Plated

## ACCESSORY MATERIALS

Coating:  Powder coated to match frame.

EXECUTION

EXAMINATION

Examine substrates and members to which the work of this section attaches or adjoins prior to frame installation.

Provide openings plumb, square and within allowable tolerances.

Provide 3/8 inch shim space at all walls

Notify Architect of any conditions which jeopardize the integrity of the proposed smoke partition, window or door system.

Do not proceed until such conditions are corrected.

INSTALLATION

See SmokeSafe™ Window & Door System Installation Manual

REPAIR AND TOUCH UP

Limited to minor repair of small scratches. Use only manufacturer’s recommended products.

Such repairs shall match original finish for quality or material and view.

Remove and replace glass that is broken, chipped, cracked, abraded, or damaged.

ADJUSTING

Adjust door function and hardware for smooth operation. Coordinate with other hardware suppliers for function and use of any other attached hardware.

PROTECTION AND CLEANING

Protect glass from damage immediately after installation by attaching crossed streamers to framing held away from glass.  Do not apply markers to glass surface.  Remove nonpermanent labels, and clean surfaces.

Do not clean with astringent cleaners. Use a clean “grit free” cloth and a small amount of mild soap and water or mild detergent.

Do not use any of the following:

Steam jets

Abrasives

Strong acidic or alkaline detergents, or surface-reactive agents

Detergents not recommended in writing by the manufacturer

Do not use any detergent above 77 degrees F

Organic solvents including but not limited to those containing ester, ketones, alcohols, aromatic compounds, glycol ether, or halogenated hydrocarbons.

Metal or hard parts of cleaning equipment must not touch the glass surface

Protect glass from contact with contaminating substances resulting from construction operations, including weld splatter.  If, despite such protection, contaminating substances do come into contact with glass, remove them immediately as recommended by glass manufacturer.

Modify paragraph below to suit Project.

Wash glass on both exposed surfaces in each area of Project not more than four days before date scheduled for inspections that establish date of Substantial Completion.  Wash glass as recommended by glass manufacturer.

end of section