Technical Glass Products has included notes in this specification to assist you in tailoring the content to your project.  These comments will appear on your screen in blue.  To hide them and view only the specification, do the following:

Click the “Office” button and then click the word “Options” OR select the “File” and then click “Options”.   Click “Display” at the left of the dialog box.  Remove the check mark from the “Hidden Text” box.  Then click “OK.”  All blue text will then be hidden.

This document is designed for use by a qualified construction specifier. Proper modifications are required to tailor this specification to your project needs.  Optional text is placed between brackets “[ ].”  Blank underlines  “__” represent areas you need to fill in with your project specific information. For assistance, call Technical Glass Products at 1-800-426-0279.

This guide specification is a supplier-specific proprietary product specification using the proprietary method of specifying applicable to project specifications and master guide specifications. This Section specifies the “Fireframes Heat Barrier Series-Bullet Resistant” a fire-rated steel frame system supplied by Technical Glass Products further described in Part 2 – Products.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Section 08 41 23 - Fire Rated STEEL FRAMED ENTRANCEs and storefronts-FIREFRAMES® HEAT BARRIER SERIES-Bullet Resistant

- GENERAL

      - SUMMARY

        - Section includes:

          - Fire rated glazing and framing systems for installation as (choose one or more as applicable) [sidelights,] [borrowed lights,] [windows,] and [Transoms] or [wall sections] in [interior] [and] [exterior] openings

Verify that Section titles referenced below are correct for this Project's Specifications;. Revise the Section number and title below to suit project requirements, specification practices and section content. Refer to CSI MasterFormat for other section numbers and titles.

Verify other nearby items are specified. These include concrete and masonry inserts, concealed flashing.

        - Related Sections:

          - Section 05 12 00 “Structural Steel Framing:” Steel attachment members

          - Section 05 50 00  “Metal Fabrications:” Steel attachment members inserts and anchors

          - Section 07 25 00 “Weather Barriers:” Perimeter air, water and vapor seal between the work of this section and adjacent construction

          - Section 07 62 00 “Sheet Metal Flashing and Trim” Flashing between this work and other work

          - Section 07 84 00 “Firestopping:” Firestops between work of this section and other fire resistive assemblies.

      - REFERENCES

Adjust lists below to suit Project. Specifically this means to delete the types of finish that are not used AAMA 2603 thru 2605 and if the system is used in interior applications all the air and water infiltration testing and standards may be removed.

        - American Architectural Manufacturers Association (AAMA)

          - AAMA 501.1-2005: Standard Test Method for Water Penetration of Windows, Curtain Walls, and Doors Using Dynamic Pressure

          - AAMA 501.2-2003: Quality Assurance and Diagnostic Water Leakage Field Check of Installed Storefronts, Curtain Walls, and Sloped Glazing Systems

          - AAMA 501.5-2005: Test Method for Thermal Cycling of Exterior Walls

          - AAMA 1503-1998: Voluntary Test Method for Thermal Transmittance and Condensation Resistance of Windows, Doors and Glazed Wall Sections

          - AAMA 2603-2002 - Voluntary Specification, Performance Requirements and Test Procedures for Pigmented Organic Coatings on Aluminum Extrusions and Panels.

          - AAMA 2604-2005 - Voluntary Specification, Performance Requirements and Test Procedures for High Performance Organic Coatings on Aluminum Extrusions and Panels.

          - AAMA 2605-2005 - Voluntary Specification, Performance Requirements and Test Procedures for Superior Performing Organic Coatings on Aluminum Extrusions and Panels.

        - American Society for Testing and Materials (ASTM):

          - Fire safety related:

            - ASTM E119:  Methods for Fire Tests of Building Construction and Materials.

            - ASTM E2010-01:  Standard Test Method for Positive Pressure Fire Tests of Window Assemblies.

          - Material related

            - ASTM A 1008/A 1008M - Standard Specification for Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength, Low Alloy, and High-Strength Low-Alloy with Improved Formability, Solution Hardened, and Bake Hardenable; 2007.

            - ASTM A 1011/A 1011M - Standard Specification for Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy and High-Strength Low-Alloy with Improved Formability, and Ultra-High Strength; 2006b.

          - Exterior related

            - ASTM E 283-04: Test Method for Determining the Rate of Air Leakage through Exterior Windows, Curtain Walls, and Doors under Specified Pressure Differences across the Specimen

            - ASTM E 330-02: Test Method for Structural Performance of Exterior Windows, Doors, Skylights and Curtain Walls by Uniform Static Air Pressure Difference Procedure A

            - ASTM E 331-04: Test Method for Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform Static Air Pressure Difference

            - ASTM E 783-02: Test Method for Field Measurement of Air Leakage through Installed Exterior Windows and Doors

            - ASTM E 1105-00: Test Method for Field Determination of Water Penetration of Installed Exterior Windows, Skylights, Doors,  and Curtain Walls by Uniform or Cyclic Static Air Pressure Difference

          - Sound related:

            - ASTM E 90-04: Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements

            - ASTM E 413-04: Standard Classification for Rating Sound Insulation

        - American Welding Society (AWS)

          - AWS D1.3 - Structural Welding Code - Sheet Steel; 2007

        - Canadian Standards

          - CAN/ULC-S101 Standard Test of Fire Endurance Tests of Building Construction and Materials

          - CAN/ULC-S106 Standard Method of Fire Tests of Window and Glass Block Assemblies

        - National Fire Protection Association (NFPA):

          - NFPA 80:  Standard for Fire Doors and Windows.

          - NFPA 251:  Standard of Methods of Fire Tests of Building Construction & Materials

          - NFPA 257:  Standard for Fire Test of Window Assemblies

        - Underwriters Laboratories, Inc. (UL):

          - UL 10 C:  Positive Pressure Fire Tests of Window & Door Assemblies

          - UL 263:  Fire tests of Building Construction and Materials

          - UL 752  Ratings of Bullet-Resistant Materials

        - American National Standards Institute (ANSI):

          - ANSI Z97.1:  Standard for Safety Glazing Materials Used in Buildings

        - Consumer Product Safety Commission (CPSC):

          - CPSC 16 CFR 120:  Safety Standard for Architectural Glazing Materials

        - American Society of Civil Engineers (ASCE)

          - ASCE 7 – Minimum Design Loads for Buildings and Other Structures; 2005

        - New York City approval

          - MEA# 242-00-M

      - DEFINITIONS

        - Manufacturer:  A firm that produces primary glass, fabricated glass or framing as defined in referenced glazing publications.

      - SUBMITTALS

        - Submit in accordance with Section <Insert Section #>.

        - Product Data:

          - Technical Information:  Submit latest edition of manufacturer’s product data providing product descriptions, technical data, Underwriters Laboratories, Inc. listings and installation instructions.

        - Shop Drawings:

          - Include plans, elevations and details of product showing component dimensions; framed opening requirements, dimensions, tolerances, and attachment to structure

        - Design Data (if engineered)

        - Hardware schedule: list of manufacture supplied hardware and verification of cylinder size complying with Section 08 71 00

        - Samples (optional):   For following products:

          - Glass sample-as provided by manufacturer

          - Sample of frame

          - Verification of sample of selected finish

        - Glazing Schedule:  Use same designations indicated on drawings for glazed openings in preparing a schedule listing glass types and thicknesses for each size opening and location.

        - Warranties: Submit manufacturer’s warranty.

        - Certificates of compliance from glass and glazing materials manufacturers attesting that glass and glazing materials furnished for project comply with requirements.

          - Separate certification will not be required for glazing materials bearing manufacturer’s permanent label designating type and thickness of glass, provided labels represent a quality control program involving a recognized certification agency or independent testing laboratory acceptable to authority having jurisdiction.

      - QUALITY ASSURANCE

        - Testing Agency Qualifications: Qualified according to

          - International Accreditation Service for a Type A Third-Party Inspection Body (Field Services ICC-ES Third-Party Inspections Standard Operating Procedures, 00-BL-S0400 and S0401)

          - International Accreditation Service for Testing Body-Building Materials and Systems

            - Fire Testing

              - ASTM Standards  E 119

              - CPSC Standards 16 CFR 1201

              - NFPA Standards 251, 252, 257

              - UL Standards 9, 10B, 10C, 1784, UL Subject 63

              - BS 476; Part 22:  1987

              - EN 1634-1

              - CAN/ULC Standards S101, S106

        - Installer Qualifications:  An experienced installer who has completed glazing similar in material, design, and extent to that indicated for this Project; whose work has resulted in glass installations with a record of successful in-service performance; and who employs glass installers for this Project who are certified under the National Glass Association Glazier Certification Program as Level 2 (Senior Glaziers) or Level 3 (Master Glaziers).

Delete paragraph above or below.  If retaining above, verify with prospective installers that they can comply with glazier certification requirements.

        - Installer Qualifications:  An experienced installer who has completed glazing similar in material, design, and extent to that indicated for Project and whose work has resulted in construction with a record of successful in-service performance.

        - Source Limitations for Glazing Accessories:  Obtain glazing accessories from one source for each product and installation method indicated.

        - Fire-Rated Window Assemblies:  Assemblies complying with NFPA 80 that are classified and labeled by UL, for fire ratings indicated, based on testing according to NFPA 257, ASTM E119.  Assemblies must be factory-welded or come complete with factory-installed mechanical joints and must not require job site fabrication.

        - Fire-Rated Wall Assemblies: Assemblies complying with ASTM E119 that are classified and labeled by UL, for fire ratings indicated, based on testing in accordance with UL 263, ASTM E119.

Adjust certification list below to suit Project.

Generally retain paragraph below unless types of glass selected do not require labeling by authorities having jurisdiction or if certification is required as well as labels.

        - Listings and Labels - Fire Rated Assemblies:  Under current follow-up service by Underwriters Laboratories® maintaining a current listing or certification. Label assemblies accordance with limits of manufacturer’s listing.

        - Regulatory Requirements:  Comply with provisions of the following:

      - DELIVERY, STORAGE AND HANDLING

        - Deliver, store and handle under provisions specified by manufacturer.

      - PROJECT CONDITIONS

        - Obtain field measurements prior to fabrication of frame units. If field measurements will not be available in a timely manner coordinate planned measurements with the work of other sections.

          - Note whether field or planned dimensions were used in the creation of the shop drawings.

        - Coordinate the work of this section with others effected including but not limited to: other interior and/or exterior envelope components beyond that provided by this section

      - WARRANTY

        - Provide the Pilkington Pyrostop® and the Fireframes® Heat Barrier Series limited five- year warranty from the date of shipment from the factory.

- PRODUCTS

Adjust options in Article below to suit Project.

      - MANUFACTURERS - FIRE RATED [WINDOW] [WALL ASSEMBLY]

        - Manufacturer Glazing Material:  “Pilkington Pyrostop®” fire-rated glazing as manufactured by the Pilkington Group and distributed by Technical Glass Products, 8107 Bracken Place SE, Snoqualmie, WA  98065 phone (800.426.0279) e-mail tgp.sales@allegion.com, web site http://www.fireglass.com

        - Frame System:  “Fireframes® Heat Barrier Series-Bullet Resistant” fire-rated [steel] frame system as manufactured and supplied by Technical Glass Products, 8107 Bracken Place SE, Snoqualmie, WA  98065 phone (800.426.0279) e-mail tgp.sales@allegion.com  web site http://www.fireglass.com

        - Substitutions:  Substitutions for Glazing Material and Frame System not permitted.

      - PERFORMANCE REQUIREMENTS Adjust fire rating minutes in paragraphs below to suit Project.

        - Fire Rating Requirements

          - Duration-- Windows:  Capable of providing a fire rating for [60] [90] [120] minutes.

          - Duration-- Walls:  Capable of providing a fire rating for [60], [90], [120] minutes

        - Delegated design: For the performance requirements listed below requiring structural design provide data, calculations and drawings signed and sealed by an engineer licensed in the state [province] where the project is located.

        - Design Requirements

          - Dimensions -- Window Assembly:

            - Perimeter framing face dimension:  3-1/8-inch at head, sill and jamb.

            - Horizontal and/or vertical mullions:  4-1/8-inch on the face.

            - Depth of perimeter and mullion:  depth varies based on rating and profile

ASTM E330 procedure A is a test method that describes the determination of the structural performance of exterior windows, skylights, and curtain walls under uniform static air pressure differences, using a test chamber. The test is intended only for evaluating the structural performance associated with the specified test specimen and not the structural performance of adjacent construction.

Member deflection is referenced from the IBC Section 24 General Requirements for Glass, article 2403.3.

        - Structural Performance

          - Design and size the system to withstand structural forces placed upon it without damage or permanent set when tested in accordance with ASTM E330 using load 1.5 times the design wind loads and of 10 seconds in duration.

          - Positive wind load: [______lbf/sq. ft.][as indicated on the drawings]

          - Negative wind Load:[______lbf/sq. ft.][as indicated on the drawings]

          - Member deflection: Limit deflection of the edge of the glass normal to the plane of the glass to [flexure limit of glass][1/175 of the glass edge length or ¾ inch, whichever is less]of any framing member

          - Accommodate movement between storefront and adjoining systems

Coordinate the lbf/sq ft with those required in the field test at the end of the section.

        - Air infiltration: Provide systems that allow a maximum air leakage through fixed glazed openings of 0.06 cfm/sq. ft. of area when tested per ASTM E 283 at a static air differential of [1.57] [6.24] lbf/sq. ft.

Coordinate the lbf/sq ft with those required in the field test at the end of the section.

        - Water Penetration

          - Under Static pressure, provide systems that do not show uncontrolled water leakage when tested according to ASTM E 331 under static pressure equal to 20 percent of positive wind-load design pressure, but not less than 6.24 lbf/sq. ft.

          - Under Dynamic pressure, provide systems that do not show uncontrolled water leakage when tested according to AAMA 501.1 under static pressure equal to 20 percent of positive wind-load design pressure, but not less than 6.24 lbf/sq. ft.

Coordinate the level of bullet resistance with the type of glazing selected in Part 2 of this specification.

        - Bullet Resistance: provide systems that meet a bullet resistance level of [I] [II] [III] and a level of 8 for the frame when tested per UL 752

      - MATERIALS - GLASS

        - Low-E Coated glass for use in insulated exterior units See Section 08 80 00

Use the paragraph above to specify the low-e coated glass in Section 08 80 00 and use the paragraph below to select glass available from Technical Glass Products. Other manufacturer’s glass will need to be shipped to Technical Glass Products for incorporation into insulated unit.

Not all low-e coated glass by all manufacturers is available for assembly by others into insulated units. Consult with  low-e glass manufacturer about availability of their low-e product for shipment to Technical Glass Products for inclusion into insulated units.

        - Fire Rated Glazing:  Composed of multiple sheets of Pilkington Optiwhite™ low iron, high-visible-light transmission glass laminated with an intumescent interlayer.

        - Impact Safety Resistance:  ANSI Z97.1 and CPSC 16CFR1201 (Cat. I and II).

Adjust list of properties below to suit Project -- these are listed in tabular form delete those columns not used.

        - Properties-Glazing

| Property | 60 minute |  | 90 and 120 minute |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Manufacturer’s designation | 60-201 | 60-261 or 60-361* | 120-202 | 120-201 | 120-201 | 120-262 or 120-362* |
| Glazing type | single | IGU | single | IGU | IGU | IGU |
| Nominal Thickness | 1-1/16” (27mm) | 1-5/8” (41mm) | 1-9/16” (40mm) | 2-7/16 (62mm) | 2-7/16 (62mm) | 2-3/8" (60 mm) [with 14 mm spacer, or 2-1/8” (54 mm) with 8 mm spacer] |
| With Anti-Spalling Film | Yes | Yes | Yes | No | Yes | Yes |
| Weight in lbs/sf | 12.9 | 15.77 | 18.64 | 25.8 | 25.8 | 21.71 |
| Daylight Transmission | 86% | 77% | 86% | 73% | 73% | 74% |
|  |  | 59-70% |  |  |  | 33-68% |
| Sound Transmission Coefficient | 44dB | 44dB | 46dB | 46dB | 46dB | 46dB |
| Bullet Resistance Rating per UL-752 | Level I | Level I | Level II | Level II | Level III | Level II |

- Note:  Care should be taken to not scratch products with surface-applied, anti-spalling film.

- * Low-E product.

        - Exterior Grade:  PVB inner layer installed towards the exterior.

        - Logo:  Each piece of fire-rated glazing shall be labeled with a permanent logo including name of product, manufacture, testing laboratory (UL), fire rating period, safety glazing standards, and date of manufacture.

        - Glazing Accessories: Manufacturer’s standard compression gaskets, spacers, setting blocks and other accessories necessary for a complete installation.

      - MATERIALS – STEEL FRAMES

Adjust list of minutes below to suit Project.

        - Steel Framing System [60 min.] [90 min] [120 min]:

          - Frame:  [Steel] profiled formed tubing permanently joined with steel bolts.

          - Insulation:  Insulate framing system against effects of fire, smoke, and heat transfer from either side. Insulate profiled steel tubing using a shell construction that incorporates Promatect-H intermediate interlayer. Firmly pack perimeter of framing system to rough opening with mineral wool fire stop insulation or appropriately rated intumescent sealant.

          - Frame meets Bullet resistance rating Level 8 per UL 752

          - Steel Glazing Beads:  Extruded steel beads with dimensions recommended by manufacturer to securely hold glazing material in place.

          - Fasteners:  Type recommended by manufacturer

          - Glazing Accessories: Set Pilkington Pyrostop glass using calcium silicate, or setting blocks.

          - Glazing Gaskets, Compounds and tapes:  Glaze Pilkington Pyrostop glass with approved EPDM glazing gaskets and [closed cell PVC tape], or [pure silicone sealant].

      - FABRICATION

        - Furnish exterior frame assemblies pre-welded.

          - When necessary, splice frames too large for shop fabrication or shipping or to fit in available building openings.

          - Fit with suitable fasteners.

        - Furnish interior frame assemblies “K-D” (or welded upon request).

          - When necessary, splice frames too large for shop fabrication or shipping or to fit in available building openings.

          - Fit with suitable fasteners.

        - Field glaze frame assemblies.

        - Fabrication Dimensions:  Fabricate fire rated assembly to field dimensions.

        - Obtain approved Shop Drawings prior to fabrication.

      - FINISHES, GENERAL

        - Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

        - Finish frames after assembly.

        - Appearance of Finished Work:  Variations in appearance of abutting or adjacent pieces are acceptable.  Noticeable variations in the same piece are not acceptable.

Powder coat finish systems offered and provided by Technical Glass Products are manufactured by Tiger Drylac which is a hybrid powder coating for interior applications based on a blend of epoxy-polyester. If used exteriorly contact your Technical Glass Product Representative for alternative finishes that provide an even higher standard of protection.

      - POWDERCOAT FINISHES

        - Finish after fabrication.

        - Appearance of Finished Work:	Variations in appearance of abutting or adjacent pieces are acceptable. Noticeable variations in the same piece are not acceptable.

        - Interior and Exterior Steel Finishes (Note: this finish is suitable for exterior exposed portions of the wall systems, including extruded aluminum covers)

          - Powder-Coat Finish: Polyester Super Durable powder coating which meets AAMA 2604 for chalking and fading. Apply manufacturer's standard powder coating finish system applied to factory-assembled frames before shipping, complying with manufacturer's recommended instructions for surface preparation including pretreatment, application, and minimum dry film thickness.

          - Color and Gloss: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

          - Acceptable Manufacturers:

            - Tiger Drylac

            - Additional manufacturers as approved by TGP

      - ACCESSORY MATERIALS

        - Bituminous Paint:  Cold-applied, asphalt-mastic paint complying with SSPC-Paint 12 requirements except containing no asbestos; formulated for [30-mil] [0.762-mm] thickness per coat.

- EXECUTION

      - EXAMINATION

        - Examine substrates and members to which the work of this section attaches or adjoins prior to frame installation.

        - Provide openings plumb, square and within allowable tolerances.

          - The manufacturer recommends 3/8 inch shim space at all walls

        - Notify Architect of any conditions which jeopardize the integrity of the proposed fire wall system.

        - Do not proceed until such conditions are corrected.

      - INSTALLATION

        - See Fireframes Heat Barrier Series Installation Manual

      - REPAIR AND TOUCH UP

        - Limited to minor repair of small scratches. Use only manufacturer’s recommended products.

          - Such repairs shall match original finish for quality or material and view.

        - Remove and replace glass that is broken, chipped, cracked, abraded, or damaged.

      - PROTECTION AND CLEANING

        - Protect glass from damage immediately after installation by attaching crossed streamers to framing held away from glass.  Do not apply markers to glass surface.  Remove nonpermanent labels, and clean surfaces.

          - Do not clean with astringent cleaners. Use a clean “grit free” cloth and a small amount of mild soap and water or mild detergent.

          - Do not use any of the following:

            - Steam jets

            - Abrasives

            - Strong acidic or alkaline detergents, or surface-reactive agents

            - Detergents not recommended in writing by the manufacturer

            - Do not use any detergent above 77 degrees F

            - Organic solvents including but not limited to those containing ester, ketones, alcohols, aromatic compounds, glycol ether, or halogenated hydrocarbons.

            - Metal or hard parts of cleaning equipment must not touch the glass surface

        - Protect glass from contact with contaminating substances resulting from construction operations, including weld splatter.  If, despite such protection, contaminating substances do come into contact with glass, remove them immediately as recommended by glass manufacturer.

Modify paragraph below to suit Project.

        - Wash glass on both exposed surfaces in each area of Project not more than four days before date scheduled for inspections that establish date of Substantial Completion.  Wash glass as recommended by glass manufacturer.

END OF SECTION