Technical Glass Products has included notes in this specification to assist you in tailoring the content to your project.  These comments will appear on your screen in blue.  To hide them and view only the specification, do the following:  Click on “Tools” on your Microsoft Word toolbar.  Under Tools, select “Options.” On the “View” tab, under “Formatting Marks,” remove the check mark from the “Hidden Text” box.  Then click “OK.”  All blue text will then be hidden.  For assistance, call Technical Glass Products at 1-800-426-0279.

This guide specification is a supplier-specific proprietary product specification using the proprietary method of specifying applicable to project specifications and master guide specifications. Optional text is indicated by brackets []; delete optional text in final copy of specification.

This Section specifies “FireLite®IGU” fire-rated or fire/impact safety-rated insulated glass units supplied by Technical Glass Products as further described in Part 2 – Products.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

SECTION 08 88 13 - FIRE-RATED GLASS – firelite® igu

- GENERAL

      - SUMMARY

        - Section Includes:

          - Fire-rated insulated glass units (IGU) installed as vision lights in fire-rated doors.

          - Fire-rated insulated glass units (IGU) installed as [transoms] [borrowed lites] [windows] in fire-rated frames.

          - [Fire-rated insulated glass units (IGU) installed in exterior applications where energy codes require an insulated product.]

          - [Fire-rated insulated glass units (IGU) installed in interior applications requiring sound reduction.]

Verify that Section titles referenced below are correct for this Project's Specifications; Section titles may have changed. Revise Section number and title below to suit project requirements, specification practices and section content. Refer to CSI MasterFormat for other section numbers and titles.

        - Related Sections include the following:

          - Section 08 11 00 – “Metal Doors and Frames”: Vision panels in [exterior] [interior] doors and [exterior] [interior] vision panel (borrowed lites) frames.

          - Section 08 14 16 – “Flush Wood Doors”:  Vision panels in interior doors.

          - Section 08 51 23 – Steel Windows.

      - references

Adjust lists below to suit Project.

        - American Society for Testing and Materials (ASTM):

          - ASTM E 774 – Standard Specification for Sealed Insulating Glass Units.

          - ASTM C920 Standard Specification for Elastomeric Joint Sealants

          - ASTM C 1036 – Standard Specification for Flat Glass.

          - ASTM C 1048 – Standard Specification for Heat-Treated Flat Glass—Kind HS, Kind FT Coated and Uncoated Glass.

          - ASTM E2010-01:  Standard Test Method for Positive Pressure Fire Tests of Window Assemblies.

        - Glass Association of North America (GANA):

          - GANA – Glazing Manual.

          - FGMA – Sealant Manual.

        - National Fire Protection Association (NFPA):

          - NFPA 80 – Fire Doors and Windows.

          - NFPA 252 – Fire Tests of Door Assemblies.

          - NFPA 257 – Fire Tests of Window Assemblies.

        - SIGMA TM-3000-90 – Vertical Glazing Guidelines.

        - Underwriters Laboratories, Inc. (UL):

          - UL 9 – Fire Tests of Window Assemblies.

          - UL 10B – Fire Tests of Door Assemblies.

          - UL 10C – Positive Pressure Fire Tests of Door Assemblies.

Following are Canadian Standards

        - Standard Council of Canada:

          - CAN/ULC-S104 Standard Method of Fire Tests of Door Assemblies

          - CAN/ULC-S106 Standard Method of Fire Tests of Window and Glass Block

        - <Insert building code name used by authority having jurisdiction>.

      - DEFINITIONS

        - Manufacturer:  A firm that produces primary glass, fabricated glass or framing as defined in referenced glazing publications.

      - SUBMITTALS

- Note:  Specify submittal requirements for fire-rated doors and fire-rated frames, including glass stops in the appropriate Sections.

        - Comply with requirements of Section 01 33 00<Insert Section #>.

        - Product data:  Submit manufacturer’s technical data for each glazing material required, including installation and maintenance instructions.

        - Certificates of compliance from glass and glazing materials manufacturers attesting that glass and glazing materials furnished for project comply with requirements. Separate certification will not be required for glazing materials bearing manufacturer’s permanent label designating type and thickness of glass, provided labels represent a quality control program involving a recognized certification agency or independent testing laboratory acceptable to authority having jurisdiction.

        - Product Test Listings:  From UL indicating fire-rated glass complies with requirements, based on comprehensive testing of current product.

        - Samples:  Submit, for verification purposes, approx. 8-inch by 10-inch sample for each type of glass indicated.

        - Insulating Glass Certification Program:  Provide insulating glass units complying with requirements indicated which are permanently marked with certification label of the following inspecting and testing agency:

          - Insulating Glass Certification Council.

          - Associated Laboratories, Inc.

      - QUALITY ASSURANCE

        - Glazing Standards:  FGMA Glazing Manual and Sealant Manual.

        - Fire Protective Rated Glass:  Each lite shall bear permanent, nonremovable label of UL certifying it for use in tested and rated fire protective assemblies.

        - Fire Protective Glazing Products for Door Assemblies:  Products identical to those tested per ASTM E2074-00, classified and labeled by UL acceptable to authorities having jurisdiction.

      - delivery, storage, and handling

        - Deliver, store, and handle materials under provisions of Section 01 60 00<Insert Section #>.

        - Deliver materials to specified destination in manufacturer or distributor’s packaging, undamaged, complete with installation instructions.

        - Store off ground, under cover, protected from weather and construction activities.

      - WARRANTY

        - Provide manufacturer's limited warranty under provision of Section 01 78 00<Insert Section #>.

- PRODUCTS

      - mANUFACTURERS- (aCCEPTABLE MANUFACTURER/PRODUCTS)

        - Manufacturer: [FireLite®] [FireLite® NT] [FireLite Plus®] as manufactured by Technical Glass Products, 8107 Bracken Place SE, Snoqualmie, WA  98065 phone (800.426.0279) e-mail tgp.sales@allegion.com, web site http://www.fireglass.com

      - PERFORMANCE REQUIREMENTS

        - Clear and wireless glass ceramic and tempered or annealed float glass material; listed for use in fire-rated or fire/impact safety-rated insulated glass units in locations with fire rating requirements ranging from 20 to 3 hours with required hose stream test.

        - Passes positive pressure test standards UL 10C.

- Note:  This product is not a barrier to radiant heat. This product does not meet test standards ASTM E 119 or UL 263. If your jurisdiction requires a “barrier to heat” product, please contact Technical Glass Products regarding Pilkington Pyrostop®.

- FireLite side may be lightly sandblasted or etched without affecting the fire rating.

      - MATERIALS

        - Primary Glass Products (AG - Annealed Glass):  ASTM C 1036, Type I (transparent, flat), [1/4 inch] [6 mm] thick float glass unless otherwise indicated:

          - Clear Float:  Class 1 (clear), Quality q3 (glazing select).

          - Tinted Float:  Class 2 (tinted heat absorbing and light reducing), Quality q3 (glazing select).  Listed shading and transmittance values are for [1/4 inch] [6 mm] thickness.

FireLite®IGU is available incorporating a variety of glass products, including, but not limited to the following:

          - Green Nonreflective:  LOF EverGreen Tint, uncoated tinted glass with shading coefficient 0.59 and average daylight transmittance 66 percent.

          - Blue-Green:  Uncoated blue-green tinted glass with shading coefficient 0.72 and average daylight transmittance 75 percent.

          - Gray:  Uncoated gray tinted glass with shading coefficient 0.65-0.67 and average daylight transmittance 44 percent.

          - Dark Gray:  Uncoated gray tinted glass with shading coefficient 0.64-0.66 and average daylight transmittance 13-15 percent.

          - Bronze:  Uncoated bronze tinted glass with shading coefficient 0.69-0.71 and average daylight transmittance 50-52 percent.

          - Blue-Green Reflective:  LOF Blue-Green Eclipse reflective glass, with coating on #2 surface, shading coefficient of 0.50 and average daylight transmittance 33 percent.

          - Grey Reflective:  LOF Grey Eclipse reflective glass, with coating on #2 surface, shading coefficient of 0.53 and average daylight transmittance 20 percent.

        - Heat-Treated Safety Glass:  ASTM C 1048:

          - TG - Tempered Glass, Clear:  Kind FT, Condition A, Type I, Class and Quality as specified for primary clear float glass.

          - TG - Tempered Glass, Tinted:  Kind FT, Condition A, Type I, Class and Quality and Color as specified for primary tinted float glass.

        - Sealed Insulating Glass Units:  ASTM E 774, Class A.

          - Nominal Thickness:  [1 inch] [25.4 mm] [3/4 inch] [19 mm].

          - Glass - Vision Units:  Two lites, one fire-rated and one tempered safety or annealed glass, as scheduled:

            - Exterior Lite:  [Tinted] [Clear] float.

            - Interior Lite:  Clear [FireLite®] [FireLite NT] with [Premium] [Standard] [Obscure] surface finish,   [FireLite Plus®] with [Premium] [Standard] finish.

Insert to suit insulated glass units with and without tinted glass; with and without coatings or gas in air space.

            - Performance:  [Insert #] percent visible light transmittance and [Insert #] percent visible light reflectance; winter nighttime U-value of [Insert #]; summer daytime U-value of [Insert #]; and solar heat gain coefficient of [Insert #].

          - Air Space Width:  Nominal 1/2 inch measured perpendicularly from surfaces of glass lites at unit's edge.

          - Sealing System:  Dual seal, 10 year limited warranty.

          - Spacer Specifications:  Manufacturer's standard stainless steel.

            - Desiccant:  Manufacturer's standard desiccant.

            - Corner Construction:  Manufacturer's standard corner construction.

      - MATERIALS-GLASS

        - Properties – [FireLite®]:

Note:  Figures are for FireLite Premium Grade. Figures will differ slightly for Standard Grade and Obscure (patterned) surface finishes.

FireLite Standard Grade polished surface quality is comparable to alternative fire-rated ceramics that are marketed as having a premium finish. FireLite Premium Grade is the industry leader for quality and is unmatched by alternative products or production methods. Both of its surfaces are ground and polished to provide superior surface quality, improving the overall clarity.  The FireLite family of products feature ultraHD® Technology for superior color, clarity and surface quality.  FireLite may be lightly sandblasted or etched on one side without affecting fire rating.

          - Thickness:  3/16 inch [5 mm].

          - Weight:  2.56 lbs/ft2 or 12.5 kg/m2

          - Approximate Visible Transmission:  88 percent.

          - Approximate Visible Reflection:  9 percent.

          - Hardness (Vicker’s Scale):  700.

          - Fire-rating:  20 minutes to 90 minutes.

          - Impact Safety Resistance:  [None].

          - Positive Pressure Test:  UL 10C; passes.

          - Surface Finish:

            - Standard Grade is polished for a surface quality that is comparable to alternative fire-rated ceramics marketed as having a premium finish.

            - Premium Grade is finish ground and polished on both surfaces to provide superior surface quality, improving overall clarity and providing a surface that is unmatched by alternative products.

            - Obscure-Patterned surface for privacy.

        - [Properties – FireLite® NT]

Figures are for FireLite NT Premium Grade. Figures will differ slightly for Standard Grade and Obscure (patterned) surface finishes.

FireLite NT Standard Grade polished surface quality is comparable to alternative fire-rated ceramics that are marketed as having a premium finish. FireLite NT Premium Grade is the industry leader for quality and is unmatched by alternative products or production methods. Both of its surfaces are ground and polished to provide superior surface quality, improving the overall clarity.  The FireLite family of products feature ultraHD® Technology for superior color, clarity and surface quality. FireLite NT may be lightly sandblasted or etched on one side without affecting fire rating.

          - [Thickness:  3/16 inch (8 mm).]

          - [Film:  3M Scotchshield Ultra Film.]

          - [Weight: 2.56 lbs/ft2 or 12.5 kg/m2]

          - [Approximate Visible Transmission:  88 percent.]

          - [Approximate Visible Reflection:  9 percent.]

          - [Hardness (Vicker's Scale):  700.]

          - [Fire-rating:  20 minutes to 3 hours for doors; 20 minutes to 90 minutes for other applications.]

          - [Impact Safety Rating:  ANSI Z97.1 and CPSC 16CFR1201 (Cat. I and II).]

          - [Positive Pressure Test:  UL 10C; passes.]

          - Surface Finish:

            - Standard Grade is polished for a surface quality that is comparable to alternative fire-rated ceramics marketed as having a premium finish.

            - Premium Grade is finish ground and polished on both surfaces to provide superior surface quality, improving overall clarity and providing a surface that is unmatched by alternative products.

            - Obscure-Patterned surface for privacy.

        - [Properties – FireLite Plus®]

Figures are for FireLite Plus Premium Grade. Figures will differ slightly for Standard Grade surface finish.

FireLite Plus Standard Grade polished surface quality is comparable to alternative fire-rated ceramics that are marketed as having a premium finish. FireLite Plus Premium Grade is the industry leader for quality and is unmatched by alternative products or production methods. Both of its surfaces are ground and polished to provide superior surface quality, improving the overall clarity.  The FireLite family of products feature ultraHD® Technology for superior color, clarity and surface quality.  FireLite Plus may be lightly sandblasted/etched or beveled on one side without affecting fire rating.

- [Thickness:  5/16 inch (8 mm)].

- [Weight:  4 lbs./sq. ft.]

- [Approximate Visible Transmission:  85 percent.]

- [Approximate Visible Reflection:  9 percent.]

- [Fire-rating:  20 minutes to 3 hours for doors; 20 minutes to 90 minutes for other applications.]

- [Impact Safety Rating:  ANSI Z97.1 and CPSC 16CFR1201 (Cat. I and II).]

- [STC Rating:  Approximately 35 dB.]

- [Positive Pressure Test:  UL 10C; passes.]

          - Surface Finish:

            - Standard Grade is polished for a surface quality that is comparable to alternative fire-rated ceramics marketed as having a premium finish.

            - Premium Grade is finish ground and polished on both surfaces to provide superior surface quality, improving overall clarity and providing a surface that is unmatched by alternative products.

        - Maximum sheet sizes based on surface finish:

          - [FireLite®] [FireLite® NT] Premium:  48 inches by 96 inches.

          - [FireLite®] [FireLite NT®] Standard:  48 inches by 96 inches.

          - [FireLite®] [FireLite NT®] Obscure:  36 inches by 96 inches.

          - [FireLite Plus®] Premium:  48 inches by 96 inches.

          - [FireLite Plus®] Standard:  48 inches by 96 inches.

        - Labeling:  Permanently label each piece of FireLite® [FireLite Plus®] with the FireLite® [FireLite Plus®] logo, UL logo and fire rating in sizes up to 3,325 sq. in., and with the FireLite® [FireLite Plus®] label only for sizes that exceed the listing (as approved by the local authority having jurisdiction).

        - Fire Rating:  Fire rating classified and labeled by UL for fire rating scheduled at opening locations on drawings, when tested in accordance with [ASTM E2010-01 [ULC Standards CAN4 S-104 and CAN4 S-106] [NPFA 252 and NFPA 257] [UL 9 and UL 10B].GLAZING COMPOUND FOR FIRE-RATED GLAZiNG MATERIALS

      - MATERIALS-GLAZING COMPOUND FOR FIRE-RATED INSULATION GLASS UNITS

- Note:  Select one the following: glazing tape, glazing compound or silicone sealant.

        - Glazing Tape:  Closed cell polyvinyl chloride (PVC) foam, coiled on release paper over adhesive on two sides, maximum water absorption by volume of 2 percent. Glass panels that exceed 1,393 sq. inches for 90-minute ratings must be glazed with fire-rated glazing tape supplied by manufacturer.

        - [Glazing Compound: DAP 33 putty.]

        - [Silicone Sealant (Not to be used with FireLite NT unless used as a cap bead/seal):  One-part neutral curing silicone, medium modulus sealant, Type S; Grade NS; Class 25 with additional movement capability of 50 percent in both extension and compression (total 100 percent); Uses (Exposure) NT*; Uses (Substrates) G, A, and O as applicable. Available Products:

          - Dow Corning 795 - Dow Corning Corp.

          - Silglaze-II 2800 - General Electric Co.

          - Spectrem 2 - Tremco Inc.]

- Per ASTM C920 Standard Specification for Elastomeric Joint Sealants: “Type” defines whether products are premixed or require mixing at the jobsite (S=single compound sealant).  “Grade” defines flow characteristics of the sealants (NS=nonsag or gunnable sealant). “Uses Exposure” defines classifications related to exposure (NT= nontraffic).  “Uses Substrates” defines where the sealants can be used (G=glass, A=aluminum, O=other).

        - Setting Blocks:  Neoprene, EPDM, or silicone; tested for compatibility with glazing compound; of 70 to 90 Shore A hardness.

        - Cleaners, Primers, and Sealers:  Type recommended by manufacturer of glass and gaskets.

      - FABRICATION

        - Fabricate glass and other glazing products in sizes required to glaze openings indicated for Project, with edge and face clearances, edge and surface conditions, and bite complying with recommendations of product manufacturer and referenced glazing standard as required to comply with system performance requirements.

- EXECUTION

      - EXAMINATION

        - Comply with referenced FGMA standards and instructions of manufacturers of glass, glazing sealants, and glazing compounds.

        - Protect glass from edge damage during handling and installation.  Inspect glass during installation and discard pieces with edge damage that could affect glass performance.

        - Set units of glass in each series with uniformity of pattern, draw, bow, and similar characteristics.

        - Cut glazing tape to length and set against permanent stops, flush with sight lines to fit openings exactly, with stretch allowance during installation.

        - Place setting blocks located at quarter points of glass with edge block no more than 6 inches from corners.

        - Glaze vertically into labeled fire-rated metal frames with same fire rating as glass and push against tape for full contact at perimeter of pane or unit.

        - Place glazing tape on free perimeter of glazing in same manner described above.

        - Install removable stop and secure without displacement of tape.

        - [Use specified glazing compound, without adulteration; bed glazing material in glazing compound; entirely fill all recess and spaces. Provide visible glazing compound with smooth and straight edges.]

        - Install in vision panels in fire-rated doors to requirements of NFPA 80.

        - Install so that appropriate [UL] [FireLite® IGU] markings remain permanently visible..

      - PROTECTION AND CLEANING

        - Protect glass from contact with contaminating substances resulting from construction operations.  Remove any such substances by method approved by glass manufacturer.

        - Wash glass on both faces not more than four days prior to date scheduled for inspections intended to establish date of substantial completion.  Wash glass by method recommended by glass manufacturer.

      - GLAZING SCHEDULE

| Rating | Assembly | Max. Exposed Area (Sq. In.) | Max. Width Of Exposed Glazing (In.) | OR | Max. Height Of Exposed Glazing (In.) | Stop Height |
| --- | --- | --- | --- | --- | --- | --- |
| 20 min. | Doors* HMS or wood** Fireframes® D.S. Other than doors HMS or wood Fireframes D.S. | 3,204 3,204 3,325 3,325 | 36 36 95 95 |  | 89 89 95 95 | 5/8” 3/4" 5/8” 3/4" |
| 45 min. | Doors* HMS or wood Fireframes D.S. Other than doors HMS or wood Fireframes D.S. | 3,204 3,204 3,325 3,325 | 36 36 95 95 |  | 89 89 95 95 | 5/8” 3/4" 5/8” 3/4" |
| 60 min. | Doors (non-temp rise)* HMS or wood Fireframes D.S. Doors (temp rise)* Other than doors HMS or wood Fireframes D.S. | 3,204 3,204 100 3,325 3,325 | 36 36 12 95 95 |  | 89 89 33 95 95 | 5/8” 3/4" 5/8” 5/8” 3/4" |
| 90 min. | Doors (non-temp rise)* Doors (temp rise)* Other than doors HMS Fireframes D.S. | 2,034 100 2,627 2,627 | 36 12 56 ½” 56 ½” |  | 56 ½” 33 56 ½” 56 ½” | 3/4" 1/2” 5/8” 3/4" |
| 3 hours | Doors* | 100 | 12 |  | 33 | 1/2” |

* Must be specified with either FireLite® NT or FireLite Plus®.

** HMS indicates hollow metal steel framing.  Fireframes® D.S. indicates Designer Series narrow profile framing available from TGP.  For wood frames, check with manufacturer for maximum tested glass sizes.

Individual lite sizes cannot exceed maximum exposed area shown above.

Special approval is required from the local authority having jurisdiction when using FireLite® in applications requiring a non-standard rating or sizes larger than those scheduled above and in paragraph 2.3, E. In such cases FireLite will be furnished with a FireLite label only.

END OF SECTION